{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Online"],"not_rendered":{"charts":1,"images":0,"macros":0,"external_links":0,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Online","index":0,"n_rows":253,"n_cols":20,"rows_kept":253,"cut":false,"hidden":false,"merged":[]}
["Minutes","°F FT","% O2x10","% COx100","% Effg","Date / time","°F AT","°F FT","% O2","ppm CO","% CO2","ratio","% Effg","% Effn","% ExAir","ppm uCO","°F AT","ppm amCO2","ppm amCO","l/min Pump"]
[null,{"$f":"AVERAGE(FT)","v":396.80588235294141},{"$f":"AVERAGE(Oxy)","v":13.689304812834223},{"$f":"AVERAGE(CO)","v":1327.4705882352941},{"$f":"AVERAGE(Effg)","v":78.539890710382537}]
[15,{"$f":"FT","v":155.6},{"$f":"Oxy*10","v":210},{"$f":"CO/100","v":0.12},{"$f":"Effg","v":0},"2009-02-23T12:18:47",69.7,155.6,21,12,null,null,null,null,null,null,69.7,null,null,0.54]
[15.5,153.80000000000001,210,0.86,0,"2009-02-23T12:19:17",70.099999999999994,153.80000000000001,21,86,null,null,null,null,null,null,70.099999999999994,null,null,0.54]
[16,164.2,207,5.16,0,"2009-02-23T12:19:47",70.7,164.2,20.7,516,null,null,null,null,null,null,70.7,null,null,0.52]
[16.5,167.7,204,7.49,0,"2009-02-23T12:20:17",70.8,167.7,20.399999999999999,749,null,null,null,null,null,null,70.8,null,null,0.43]
[17,177.1,198,10.79,63.5,"2009-02-23T12:20:47",71.599999999999994,177.1,19.8,1079,1.1100000000000001,9.69E-2,63.5,67.400000000000006,1722.5,19665,71.599999999999994,null,null,0.41]
[17.5,191.5,192,9.42,72.099999999999994,"2009-02-23T12:21:17",71.400000000000006,191.5,19.2,942,1.73,5.45E-2,72.099999999999994,76.599999999999994,1074.5,11064,71.400000000000006,null,null,0.37]
[18,197.4,194,9.66,66.599999999999994,"2009-02-23T12:21:47",56,197.4,19.399999999999999,966,1.59,6.0699999999999997E-2,66.599999999999994,70.7,1174.7,12314,56,null,null,0.31]
[18.5,206.8,192,11.41,67.3,"2009-02-23T12:22:17",57,206.8,19.2,1141,1.76,6.4799999999999996E-2,67.3,71.5,1052.5999999999999,13151,57,null,null,0.27]
[19,218.5,187,10.53,71.5,"2009-02-23T12:22:47",58.5,218.5,18.7,1053,2.21,4.7699999999999999E-2,71.5,75.900000000000006,819.6,9683,58.5,null,null,0.23]
[19.5,224,181,9.92,75.8,"2009-02-23T12:23:17",57.8,224,18.100000000000001,992,2.85,3.4799999999999998E-2,75.8,80.5,613.1,7074,57.8,null,null,0.21]
[20,227.3,176,10.29,77.5,"2009-02-23T12:23:47",55.7,227.3,17.600000000000001,1029,3.26,3.15E-2,77.5,82.3,522.1,6402,55.7,null,null,0.23]
[20.5,231.4,176,11.23,76.599999999999994,"2009-02-23T12:24:17",50.8,231.4,17.600000000000001,1123,3.26,3.44E-2,76.599999999999994,81.3,522.29999999999995,6988,50.8,null,null,0.24]
[21,248.3,174,9.24,77.3,"2009-02-23T12:24:47",60.1,248.3,17.399999999999999,924,3.48,2.6599999999999999E-2,77.3,82.1,483.7,5394,60.1,null,null,0.25]
[21.5,249.2,167,5.4,80,"2009-02-23T12:25:17",55.8,249.2,16.7,540,4.1500000000000004,1.2999999999999999E-2,80,85,388.6,2639,55.8,null,null,0.26]
[22,250.2,164,5.29,81.2,"2009-02-23T12:25:47",59.6,250.2,16.399999999999999,529,4.49,1.18E-2,81.2,86.2,351.8,2390,59.6,null,null,0.26]
[22.5,247.4,171,6.23,79.2,"2009-02-23T12:26:17",63.3,247.4,17.100000000000001,623,3.74,1.67E-2,79.2,84.1,443.2,3384,63.3,null,null,0.26]
[23,247,172,8.36,78.900000000000006,"2009-02-23T12:26:47",65.2,247,17.2,836,3.7,2.2599999999999999E-2,78.900000000000006,83.8,449.4,4593,65.2,null,null,0.26]
[23.5,244.5,171,7.96,79.400000000000006,"2009-02-23T12:27:17",65.400000000000006,244.5,17.100000000000001,796,3.76,2.1100000000000001E-2,79.400000000000006,84.3,439.2,4292,65.400000000000006,null,null,0.27]
[24,252.7,172,7.63,78.599999999999994,"2009-02-23T12:27:47",65.900000000000006,252.7,17.2,763,3.69,2.07E-2,78.599999999999994,83.5,450,4196,65.900000000000006,null,null,0.27]
[24.5,252.3,173,8.01,78.099999999999994,"2009-02-23T12:28:17",65.599999999999994,252.3,17.3,801,3.59,2.23E-2,78.099999999999994,83,465.6,4531,65.599999999999994,null,null,0.28000000000000003]
[25,258.10000000000002,178,7.98,75.400000000000006,"2009-02-23T12:28:47",66.599999999999994,258.10000000000002,17.8,798,3.12,2.5600000000000001E-2,75.400000000000006,80.099999999999994,550.9,5195,66.599999999999994,null,null,0.28999999999999998]
[25.5,251.4,177,8.2200000000000006,76.2,"2009-02-23T12:29:17",66.8,251.4,17.7,822,3.16,2.5999999999999999E-2,76.2,80.900000000000006,543.1,5286,66.8,null,null,0.28999999999999998]
[26,254.5,176,8.0299999999999994,76.5,"2009-02-23T12:29:47",66.7,254.5,17.600000000000001,803,3.26,2.46E-2,76.5,81.3,521.79999999999995,4993,66.7,null,null,0.28999999999999998]
[26.5,259.10000000000002,174,4.8099999999999996,77.900000000000006,"2009-02-23T12:30:17",66.900000000000006,259.10000000000002,17.399999999999999,481,3.52,1.37E-2,77.900000000000006,82.7,477.2,2776,66.900000000000006,null,null,0.28999999999999998]
[27,261.5,170,3.41,79.400000000000006,"2009-02-23T12:30:47",67.099999999999994,261.5,17,341,3.9,8.6999999999999994E-3,79.400000000000006,84.3,420.4,1775,67.099999999999994,null,null,0.28000000000000003]
[27.5,269.89999999999998,166,3.31,80.099999999999994,"2009-02-23T12:31:17",67,269.89999999999998,16.600000000000001,331,4.28,7.7000000000000002E-3,80.099999999999994,85,374.2,1570,67,null,null,0.27]
[28,276.89999999999998,161,4.03,80.900000000000006,"2009-02-23T12:31:47",66.7,276.89999999999998,16.100000000000001,403,4.76,8.5000000000000006E-3,80.900000000000006,85.9,326.10000000000002,1717,66.7,null,null,0.25]
[28.5,279.60000000000002,160,3.77,80.8,"2009-02-23T12:32:17",66.400000000000006,279.60000000000002,16,377,4.8099999999999996,7.7999999999999996E-3,80.8,85.8,322.39999999999998,1592,66.400000000000006,null,null,0.24]
[29,284.7,151,3.16,82.6,"2009-02-23T12:32:47",66.400000000000006,284.7,15.1,316,5.73,5.4999999999999997E-3,82.6,87.7,254.4,1120,66.400000000000006,null,null,0.23]
[29.5,285.39999999999998,143,3.43,83.8,"2009-02-23T12:33:17",66.7,285.39999999999998,14.3,343,6.5,5.3E-3,83.8,89,212.5,1072,66.7,null,null,0.22]
[30,288,153,3.29,82.1,"2009-02-23T12:33:47",66.900000000000006,288,15.3,329,5.55,5.8999999999999999E-3,82.1,87.2,265.8,1203,66.900000000000006,null,null,0.22]
[30.5,292.89999999999998,155,4.09,81.400000000000006,"2009-02-23T12:34:17",66.599999999999994,292.89999999999998,15.5,409,5.36,7.6E-3,81.400000000000006,86.4,278.60000000000002,1548,66.599999999999994,null,null,0.21]
[31,300.60000000000002,152,4.7,81.5,"2009-02-23T12:34:47",67.099999999999994,300.60000000000002,15.2,470,5.61,8.3999999999999995E-3,81.5,86.5,261.89999999999998,1701,67.099999999999994,null,null,0.19]
[31.5,294.7,147,3.94,82.7,"2009-02-23T12:35:17",67.099999999999994,294.7,14.7,394,6.07,6.4999999999999997E-3,82.7,87.8,234.4,1317,67.099999999999994,null,null,0.19]
[32,{"$f":"FT","v":308.10000000000002},{"$f":"Oxy*10","v":150},{"$f":"CO/100","v":4.4800000000000004},{"$f":"Effg","v":81.599999999999994},"2009-02-23T12:35:47",68.400000000000006,308.10000000000002,15,448,5.8,7.7000000000000002E-3,81.599999999999994,86.6,249.8,1567,68.400000000000006,null,null,0.19]
[32.5,301.89999999999998,147,4.37,82.5,"2009-02-23T12:36:17",68.2,301.89999999999998,14.7,437,6.13,7.1000000000000004E-3,82.5,87.6,230.9,1446,68.2,null,null,0.18]
[33,301.39999999999998,144,2.4300000000000002,83.1,"2009-02-23T12:36:47",67.5,301.39999999999998,14.4,243,6.4,3.8E-3,83.1,88.2,217.1,771,67.5,null,null,0.18]
[33.5,307.60000000000002,145,2.4300000000000002,82.6,"2009-02-23T12:37:17",67.599999999999994,307.60000000000002,14.5,243,6.29,3.8999999999999998E-3,82.6,87.7,222.9,785,67.599999999999994,null,null,0.17]
[34,312.39999999999998,144,3.14,82.6,"2009-02-23T12:37:47",68.7,312.39999999999998,14.4,314,6.43,4.8999999999999998E-3,82.6,87.7,215.9,992,68.7,null,null,0.15]
[34.5,314.3,134,3.51,83.8,"2009-02-23T12:38:17",69.3,314.3,13.4,351,7.31,4.7999999999999996E-3,83.8,89,177.5,974,69.3,null,null,0.12]
[35,318.7,130,3.99,84.1,"2009-02-23T12:38:47",69.599999999999994,318.7,13,399,7.71,5.1999999999999998E-3,84.1,89.3,163.30000000000001,1051,69.599999999999994,null,null,0.12]
[35.5,319.10000000000002,137,3.65,83.2,"2009-02-23T12:39:17",68.3,319.10000000000002,13.7,365,7.02,5.1999999999999998E-3,83.2,88.3,189,1055,68.3,null,null,0.12]
[36,316,141,3.35,82.8,"2009-02-23T12:39:47",68.099999999999994,316,14.1,335,6.67,5.0000000000000001E-3,82.8,87.9,204.1,1019,68.099999999999994,null,null,0.11]
[36.5,316.89999999999998,143,2.98,82.5,"2009-02-23T12:40:17",68.900000000000006,316.89999999999998,14.3,298,6.45,4.5999999999999999E-3,82.5,87.6,214.6,937,68.900000000000006,null,null,0.11]
[37,318.10000000000002,144,3.33,82.3,"2009-02-23T12:40:47",69,318.10000000000002,14.4,333,6.36,5.1999999999999998E-3,82.3,87.4,219.2,1063,69,null,null,0.11]
[37.5,324.60000000000002,144,3.24,82,"2009-02-23T12:41:17",69,324.60000000000002,14.4,324,6.36,5.1000000000000004E-3,82,87.1,219.1,1034,69,null,null,0.1]
[38,329.4,142,3.42,82.2,"2009-02-23T12:41:47",68.599999999999994,329.4,14.2,342,6.61,5.1999999999999998E-3,82.2,87.2,207.1,1050,68.599999999999994,null,null,0.08]
[38.5,337.4,132,6.26,83.1,"2009-02-23T12:42:17",69.5,337.4,13.2,626,7.57,8.3000000000000001E-3,83.1,88.2,168.1,1679,69.5,null,null,0.06]
[39,340.3,120,8.8800000000000008,84.1,"2009-02-23T12:42:47",69.2,340.3,12,888,8.75,1.0200000000000001E-2,84.1,89.3,132.1,2061,69.2,null,null,0.06]
[39.5,343.4,109,16.54,84.5,"2009-02-23T12:43:17",68.900000000000006,343.4,10.9,1654,9.7200000000000006,1.7000000000000001E-2,84.5,89.7,108.9,3455,68.900000000000006,null,null,0.06]
[40,366.6,127,9.3800000000000008,82.3,"2009-02-23T12:43:47",68,366.6,12.7,938,8.0299999999999994,1.17E-2,82.3,87.4,152.9,2372,68,null,null,0.57999999999999996]
[40.5,364.8,105,22.05,83.9,"2009-02-23T12:44:17",68,364.8,10.5,2205,10.16,2.1700000000000001E-2,83.9,89.1,99.8,4405,68,null,null,0.55000000000000004]
[41,362.2,106,21.65,83.9,"2009-02-23T12:44:47",69.2,362.2,10.6,2165,10.039999999999999,2.1600000000000001E-2,83.9,89.1,102.2,4377,69.2,null,null,0.54]
[41.5,349.6,108,22.31,84.1,"2009-02-23T12:45:17",69.400000000000006,349.6,10.8,2231,9.84,2.2700000000000001E-2,84.1,89.3,106.2,4601,69.400000000000006,null,null,0.54]
[42,363.3,108,23.21,83.7,"2009-02-23T12:45:47",69.3,363.3,10.8,2321,9.84,2.3599999999999999E-2,83.7,88.8,106.2,4787,69.3,null,null,0.54]
[42.5,362.7,105,28.43,83.7,"2009-02-23T12:46:17",69.7,362.7,10.5,2843,10.18,2.7900000000000001E-2,83.7,88.9,99.3,5667,69.7,null,null,0.54]
[43,390.7,102,26.7,83.3,"2009-02-23T12:46:47",70.2,390.7,10.199999999999999,2670,10.45,2.5600000000000001E-2,83.3,88.4,94.3,5189,70.2,null,null,0.53]
[43.5,380.1,97,30.43,83.8,"2009-02-23T12:47:17",71.3,380.1,9.6999999999999993,3043,10.91,2.7900000000000001E-2,83.8,89,86.1,5664,71.3,null,null,0.52]
[44,373.7,94,32.659999999999997,84.2,"2009-02-23T12:47:47",71,373.7,9.4,3266,11.24,2.9000000000000001E-2,84.2,89.4,80.5,5897,71,null,null,0.5]
[44.5,388.1,97,27.47,83.7,"2009-02-23T12:48:17",70.400000000000006,388.1,9.6999999999999993,2747,10.9,2.52E-2,83.7,88.9,86.2,5116,70.400000000000006,null,null,0.48]
[45,385.7,101,16.86,84,"2009-02-23T12:48:47",70,385.7,10.1,1686,10.54,1.6E-2,84,89.2,92.6,3248,70,null,null,0.42]
[45.5,384,107,13.76,83.6,"2009-02-23T12:49:17",70.400000000000006,384,10.7,1376,9.93,1.3899999999999999E-2,83.6,88.8,104.5,2814,70.400000000000006,null,null,0.4]
[46,386.6,112,15.48,83,"2009-02-23T12:49:47",70.400000000000006,386.6,11.2,1548,9.4600000000000009,1.6400000000000001E-2,83,88.2,114.5,3321,70.400000000000006,null,null,0.38]
[46.5,389.3,113,14.3,82.9,"2009-02-23T12:50:17",69.400000000000006,389.3,11.3,1430,9.3800000000000008,1.52E-2,82.9,88,116.5,3096,69.400000000000006,null,null,0.39]
[47,390.5,115,16.39,82.5,"2009-02-23T12:50:47",70.5,390.5,11.5,1639,9.17,1.7899999999999999E-2,82.5,87.6,121.4,3630,70.5,null,null,0.38]
[47.5,386.9,114,21.29,82.6,"2009-02-23T12:51:17",71,386.9,11.4,2129,9.31,2.29E-2,82.6,87.7,118.1,4643,71,null,null,0.36]
[48,409.8,112,20.329999999999998,82,"2009-02-23T12:51:47",70.8,409.8,11.2,2033,9.44,2.1499999999999998E-2,82,87.1,115,4371,70.8,null,null,0.34]
[48.5,415.8,103,50,81.2,"2009-02-23T12:52:17",68.400000000000006,415.8,10.3,5000,10.31,4.8500000000000001E-2,81.2,86.3,96.9,9847,68.400000000000006,null,null,0.26]
[49,422.3,105,37.67,81.5,"2009-02-23T12:52:47",69.2,422.3,10.5,3767,10.19,3.6999999999999998E-2,81.5,86.6,99.2,7504,69.2,null,null,0.23]
[49.5,420.2,107,31.82,81.7,"2009-02-23T12:53:17",69.8,420.2,10.7,3182,9.9600000000000009,3.2000000000000001E-2,81.7,86.7,103.9,6489,69.8,null,null,0.22]
[50,434.6,107,27.44,81.400000000000006,"2009-02-23T12:53:47",68.900000000000006,434.6,10.7,2744,9.9600000000000009,2.75E-2,81.400000000000006,86.5,103.7,5590,68.900000000000006,null,null,0.22]
[50.5,422.7,108,24.02,81.900000000000006,"2009-02-23T12:54:17",70.3,422.7,10.8,2402,9.86,2.4400000000000002E-2,81.900000000000006,87,105.9,4945,70.3,null,null,0.21]
[51,429.7,110,21.69,81.599999999999994,"2009-02-23T12:54:47",70.099999999999994,429.7,11,2169,9.66,2.2499999999999999E-2,81.599999999999994,86.6,110.2,4558,70.099999999999994,null,null,0.21]
[51.5,428.2,112,19.399999999999999,81.5,"2009-02-23T12:55:17",70.099999999999994,428.2,11.2,1940,9.48,2.0500000000000001E-2,81.5,86.6,114.2,4156,70.099999999999994,null,null,0.2]
[52,437.1,111,16.64,81.5,"2009-02-23T12:55:47",70.900000000000006,437.1,11.1,1664,9.5399999999999991,1.7399999999999999E-2,81.5,86.5,112.8,3542,70.900000000000006,null,null,0.2]
[52.5,433.3,111,16.53,81.7,"2009-02-23T12:56:17",70.7,433.3,11.1,1653,9.61,1.72E-2,81.7,86.7,111.2,3491,70.7,null,null,0.2]
[53,429,111,23.01,81.400000000000006,"2009-02-23T12:56:47",71.599999999999994,429,11.1,2301,9.5299999999999994,2.41E-2,81.400000000000006,86.5,112.9,4900,71.599999999999994,null,null,0.2]
[53.5,427.2,112,19.78,81.599999999999994,"2009-02-23T12:57:17",71.8,427.2,11.2,1978,9.4499999999999993,2.0899999999999998E-2,81.599999999999994,86.6,114.9,4250,71.8,null,null,0.19]
[54,427,111,24.82,81.400000000000006,"2009-02-23T12:57:47",71.900000000000006,427,11.1,2482,9.5500000000000007,2.5999999999999999E-2,81.400000000000006,86.5,112.6,5276,71.900000000000006,null,null,0.18]
[54.5,426,111,20.65,81.7,"2009-02-23T12:58:17",72,426,11.1,2065,9.59,2.1499999999999998E-2,81.7,86.8,111.6,4369,72,null,null,0.18]
[55,419.9,105,16.71,82.8,"2009-02-23T12:58:47",74,419.9,10.5,1671,10.18,1.6400000000000001E-2,82.8,87.9,99.4,3331,74,null,null,0.18]
[55.5,436.5,106,14.68,82.3,"2009-02-23T12:59:17",75,436.5,10.6,1468,10.050000000000001,1.46E-2,82.3,87.4,101.9,2964,75,null,null,0.18]
[56,424.6,102,15.83,83,"2009-02-23T12:59:47",75.2,424.6,10.199999999999999,1583,10.46,1.5100000000000001E-2,83,88.1,94.2,3074,75.2,null,null,0.17]
[56.5,430.2,101,20.5,82.7,"2009-02-23T13:00:17",74.099999999999994,430.2,10.1,2050,10.54,1.95E-2,82.7,87.8,92.7,3950,74.099999999999994,null,null,0.17]
[57,430,103,23.32,82.3,"2009-02-23T13:00:47",72.3,430,10.3,2332,10.37,2.2499999999999999E-2,82.3,87.4,95.8,4566,72.3,null,null,0.18]
[57.5,438.1,105,21.42,82,"2009-02-23T13:01:17",73.900000000000006,438.1,10.5,2142,10.119999999999999,2.12E-2,82,87,100.6,4297,73.900000000000006,null,null,0.16]
[58,440.1,108,23.39,81.599999999999994,"2009-02-23T13:01:47",74.8,440.1,10.8,2339,9.9,2.3599999999999999E-2,81.599999999999994,86.6,105,4795,74.8,null,null,0.15]
[58.5,438.7,108,23.69,81.599999999999994,"2009-02-23T13:02:17",75.5,438.7,10.8,2369,9.91,2.3900000000000001E-2,81.599999999999994,86.7,104.9,4854,75.5,null,null,0.14000000000000001]
[59,433.9,108,23.45,81.8,"2009-02-23T13:02:47",76.2,433.9,10.8,2345,9.89,2.3699999999999999E-2,81.8,86.9,105.3,4815,76.2,null,null,0.14000000000000001]
[59.5,436.7,111,22.69,81.400000000000006,"2009-02-23T13:03:17",76.5,436.7,11.1,2269,9.57,2.3699999999999999E-2,81.400000000000006,86.4,112.2,4815,76.5,null,null,0.16]
[60,441.8,111,19.420000000000002,81.5,"2009-02-23T13:03:47",76.400000000000006,441.8,11.1,1942,9.6199999999999992,2.0199999999999999E-2,81.5,86.5,111.1,4100,76.400000000000006,null,null,0.13]
[60.5,443.8,110,14.6,81.7,"2009-02-23T13:04:17",75.7,443.8,11,1460,9.65,1.5100000000000001E-2,81.7,86.7,110.4,3072,75.7,null,null,0.13]
[61,434.8,110,13.52,82.1,"2009-02-23T13:04:47",77.599999999999994,434.8,11,1352,9.69,1.4E-2,82.1,87.2,109.5,2832,77.599999999999994,null,null,0.12]
[61.5,437.2,112,12.69,81.900000000000006,"2009-02-23T13:05:17",76,437.2,11.2,1269,9.52,1.3299999999999999E-2,81.900000000000006,86.9,113.2,2706,76,null,null,0.12]
[62,453.1,112,8.66,81.5,"2009-02-23T13:05:47",76.900000000000006,453.1,11.2,866,9.4499999999999993,9.1999999999999998E-3,81.5,86.6,114.9,1861,76.900000000000006,null,null,0.14000000000000001]
[62.5,446.8,115,5.59,81.400000000000006,"2009-02-23T13:06:17",72.7,446.8,11.5,559,9.17,6.1000000000000004E-3,81.400000000000006,86.5,121.4,1238,72.7,null,null,0.13]
[63,437.2,109,19.010000000000002,81.7,"2009-02-23T13:06:47",74.8,437.2,10.9,1901,9.75,1.95E-2,81.7,86.8,108.2,3957,74.8,null,null,0.13]
[63.5,439.8,105,26.33,81.8,"2009-02-23T13:07:17",76.7,439.8,10.5,2633,10.18,2.5899999999999999E-2,81.8,86.9,99.5,5253,76.7,null,null,0.16]
[64,{"$f":"FT","v":439.2},{"$f":"Oxy*10","v":107},{"$f":"CO/100","v":22.16},{"$f":"Effg","v":81.8},"2009-02-23T13:07:47",76.099999999999994,439.2,10.7,2216,9.98,2.2200000000000001E-2,81.8,86.9,103.3,4506,76.099999999999994,null,null,0.15]
[64.5,441.9,109,20.13,81.5,"2009-02-23T13:08:17",73.8,441.9,10.9,2013,9.7200000000000006,2.07E-2,81.5,86.5,108.8,4204,73.8,null,null,0.15]
[65,449.1,109,14.94,81.5,"2009-02-23T13:08:47",72.8,449.1,10.9,1494,9.7200000000000006,1.54E-2,81.5,86.5,108.9,3122,72.8,null,null,0.16]
[65.5,455.3,113,12.39,81.099999999999994,"2009-02-23T13:09:17",72.900000000000006,455.3,11.3,1239,9.4,1.32E-2,81.099999999999994,86.1,115.9,2676,72.900000000000006,null,null,0.18]
[66,447.8,115,10.49,81.099999999999994,"2009-02-23T13:09:47",72.900000000000006,447.8,11.5,1049,9.1999999999999993,1.14E-2,81.099999999999994,86.2,120.8,2316,72.900000000000006,null,null,0.18]
[66.5,450.9,117,10.77,80.8,"2009-02-23T13:10:17",73.2,450.9,11.7,1077,9.01,1.2E-2,80.8,85.8,125.4,2428,73.2,null,null,0.18]
[67,457.7,121,10.75,80.2,"2009-02-23T13:10:47",75.2,457.7,12.1,1075,8.64,1.24E-2,80.2,85.1,134.80000000000001,2524,75.2,null,null,0.17]
[67.5,459.6,119,9.2100000000000009,80.400000000000006,"2009-02-23T13:11:17",76.5,459.6,11.9,921,8.7899999999999991,1.0500000000000001E-2,80.400000000000006,85.4,130.80000000000001,2126,76.5,null,null,0.21]
[68,452.3,124,8.68,80,"2009-02-23T13:11:47",76.599999999999994,452.3,12.4,868,8.32,1.04E-2,80,85,143.9,2117,76.599999999999994,null,null,0.19]
[68.5,456.7,122,8.16,80.2,"2009-02-23T13:12:17",76.2,456.7,12.2,816,8.5399999999999991,9.5999999999999992E-3,80.2,85.2,137.80000000000001,1940,76.2,null,null,0.19]
[69,453.7,123,7.34,80.2,"2009-02-23T13:12:47",75.5,453.7,12.3,734,8.43,8.6999999999999994E-3,80.2,85.2,140.9,1768,75.5,null,null,0.19]
[69.5,463.1,126,7.82,79.400000000000006,"2009-02-23T13:13:17",76.599999999999994,463.1,12.6,782,8.1199999999999992,9.5999999999999992E-3,79.400000000000006,84.3,149.9,1954,76.599999999999994,null,null,0.2]
[70,455.6,125,7.2,79.7,"2009-02-23T13:13:47",75.099999999999994,455.6,12.5,720,8.18,8.8000000000000005E-3,79.7,84.7,148.19999999999999,1787,75.099999999999994,null,null,0.21]
[70.5,450.9,128,6.81,79.5,"2009-02-23T13:14:17",76.3,450.9,12.8,681,7.89,8.6E-3,79.5,84.4,157.30000000000001,1752,76.3,null,null,0.22]
[71,457.2,130,6.06,79.099999999999994,"2009-02-23T13:14:47",77.400000000000006,457.2,13,606,7.74,7.7999999999999996E-3,79.099999999999994,84,162.30000000000001,1590,77.400000000000006,null,null,0.23]
[71.5,456.9,128,5.3,79.400000000000006,"2009-02-23T13:15:17",76.900000000000006,456.9,12.8,530,7.89,6.7000000000000002E-3,79.400000000000006,84.3,157.19999999999999,1363,76.900000000000006,null,null,0.24]
[72,459.4,126,4.5,79.7,"2009-02-23T13:15:47",78,459.4,12.6,450,8.09,5.5999999999999999E-3,79.7,84.7,151,1129,78,null,null,0.23]
[72.5,456.8,127,4.78,79.599999999999994,"2009-02-23T13:16:17",76.900000000000006,456.8,12.7,478,7.99,6.0000000000000001E-3,79.599999999999994,84.6,154,1214,76.900000000000006,null,null,0.22]
[73,460.9,131,4.58,78.900000000000006,"2009-02-23T13:16:47",77.2,460.9,13.1,458,7.64,6.0000000000000001E-3,78.900000000000006,83.8,165.8,1217,77.2,null,null,0.21]
[73.5,469.1,133,4.82,78.099999999999994,"2009-02-23T13:17:17",77.599999999999994,469.1,13.3,482,7.41,6.4999999999999997E-3,78.099999999999994,83,174,1321,77.599999999999994,null,null,0.2]
[74,460.8,134,4.5999999999999996,78.400000000000006,"2009-02-23T13:17:47",78.900000000000006,460.8,13.4,460,7.35,6.3E-3,78.400000000000006,83.3,176.1,1270,78.900000000000006,null,null,0.2]
[74.5,455.3,135,4.5199999999999996,78.400000000000006,"2009-02-23T13:18:17",76.5,455.3,13.5,452,7.26,6.1999999999999998E-3,78.400000000000006,83.2,179.5,1263,76.5,null,null,0.19]
[75,455.5,133,8.5500000000000007,78.5,"2009-02-23T13:18:47",77.7,455.5,13.3,855,7.46,1.15E-2,78.5,83.4,172.1,2326,77.7,null,null,0.19]
[75.5,451.9,130,8.81,79.099999999999994,"2009-02-23T13:19:17",75.7,451.9,13,881,7.75,1.14E-2,79.099999999999994,84,162,2308,75.7,null,null,0.14000000000000001]
[76,462.6,129,10.63,78.7,"2009-02-23T13:19:47",75.599999999999994,462.6,12.9,1063,7.83,1.3599999999999999E-2,78.7,83.6,159.30000000000001,2757,75.599999999999994,null,null,0.14000000000000001]
[76.5,464.2,130,9.94,78.5,"2009-02-23T13:20:17",75.400000000000006,464.2,13,994,7.71,1.29E-2,78.5,83.3,163.19999999999999,2616,75.400000000000006,null,null,0.14000000000000001]
[77,466.7,130,10.42,78.3,"2009-02-23T13:20:47",76.2,466.7,13,1042,7.7,1.35E-2,78.3,83.2,163.69999999999999,2748,76.2,null,null,0.17]
[77.5,466.8,130,9.9700000000000006,78.5,"2009-02-23T13:21:17",76.8,466.8,13,997,7.75,1.29E-2,78.5,83.3,162,2613,76.8,null,null,0.13]
[78,467.9,130,8.0399999999999991,78.599999999999994,"2009-02-23T13:21:47",77.400000000000006,467.9,13,804,7.78,1.03E-2,78.599999999999994,83.5,161.1,2099,77.400000000000006,null,null,0.16]
[78.5,460.6,132,6.31,78.7,"2009-02-23T13:22:17",77.8,460.6,13.2,631,7.59,8.3000000000000001E-3,78.7,83.6,167.6,1688,77.8,null,null,0.17]
[79,463.2,131,5.34,78.7,"2009-02-23T13:22:47",76,463.2,13.1,534,7.63,7.0000000000000001E-3,78.7,83.6,166,1420,76,null,null,0.17]
[79.5,474.6,132,4.41,78.099999999999994,"2009-02-23T13:23:17",73.7,474.6,13.2,441,7.55,5.7999999999999996E-3,78.099999999999994,82.9,168.8,1185,73.7,null,null,0.17]
[80,471.2,134,3.87,78,"2009-02-23T13:23:47",75.3,471.2,13.4,387,7.37,5.3E-3,78,82.8,175.6,1067,75.3,null,null,0.16]
[80.5,469.8,135,3.81,77.8,"2009-02-23T13:24:17",76.599999999999994,469.8,13.5,381,7.22,5.3E-3,77.8,82.6,181,1071,76.599999999999994,null,null,0.16]
[81,470.7,136,3.81,77.599999999999994,"2009-02-23T13:24:47",78.5,470.7,13.6,381,7.13,5.3E-3,77.599999999999994,82.4,184.9,1085,78.5,null,null,0.16]
[81.5,466.9,138,3.96,77.5,"2009-02-23T13:25:17",78.599999999999994,466.9,13.8,396,6.99,5.7000000000000002E-3,77.5,82.3,190.4,1150,78.599999999999994,null,null,0.16]
[82,470.8,139,4.07,76.900000000000006,"2009-02-23T13:25:47",76.8,470.8,13.9,407,6.85,5.8999999999999999E-3,76.900000000000006,81.7,196.4,1206,76.8,null,null,0.17]
[82.5,467.6,139,4.3899999999999997,77,"2009-02-23T13:26:17",74,467.6,13.9,439,6.9,6.4000000000000003E-3,77,81.8,194.1,1291,74,null,null,0.18]
[83,460.2,138,3.91,77.599999999999994,"2009-02-23T13:26:47",77.900000000000006,460.2,13.8,391,6.92,5.7000000000000002E-3,77.599999999999994,82.4,193.4,1147,77.900000000000006,null,null,0.2]
[83.5,474.3,138,3.9,77,"2009-02-23T13:27:17",78.599999999999994,474.3,13.8,390,6.92,5.5999999999999999E-3,77,81.8,193.5,1145,78.599999999999994,null,null,0.2]
[84,461.6,140,3.96,77.2,"2009-02-23T13:27:47",78,461.6,14,396,6.79,5.7999999999999996E-3,77.2,82,199,1184,78,null,null,0.21]
[84.5,468.3,140,3.78,77,"2009-02-23T13:28:17",78.599999999999994,468.3,14,378,6.78,5.5999999999999999E-3,77,81.7,199.6,1132,78.599999999999994,null,null,0.21]
[85,469.1,142,4.3099999999999996,76.5,"2009-02-23T13:28:47",78.400000000000006,469.1,14.2,431,6.61,6.4999999999999997E-3,76.5,81.2,206.9,1323,78.400000000000006,null,null,0.21]
[85.5,467.4,143,4.8899999999999997,76.3,"2009-02-23T13:29:17",79.3,467.4,14.3,489,6.52,7.4999999999999997E-3,76.3,81.099999999999994,211.4,1523,79.3,null,null,0.21]
[86,477.4,144,5.13,75.7,"2009-02-23T13:29:47",81.099999999999994,477.4,14.4,513,6.4,8.0000000000000002E-3,75.7,80.3,217,1626,81.099999999999994,null,null,0.21]
[86.5,477.2,146,5.35,74.8,"2009-02-23T13:30:17",76.3,477.2,14.6,535,6.16,8.6999999999999994E-3,74.8,79.400000000000006,229.3,1762,76.3,null,null,0.21]
[87,470.3,144,5.65,75.8,"2009-02-23T13:30:47",78.2,470.3,14.4,565,6.42,8.8000000000000005E-3,75.8,80.5,216.1,1786,78.2,null,null,0.21]
[87.5,474.3,145,5.74,75.400000000000006,"2009-02-23T13:31:17",77.3,474.3,14.5,574,6.33,9.1000000000000004E-3,75.400000000000006,80,220.9,1842,77.3,null,null,0.21]
[88,473.4,145,6.1,75.2,"2009-02-23T13:31:47",78.2,473.4,14.5,610,6.26,9.7000000000000003E-3,75.2,79.900000000000006,224.2,1978,78.2,null,null,0.22]
[88.5,479.8,148,6.46,74.099999999999994,"2009-02-23T13:32:17",80.099999999999994,479.8,14.8,646,5.97,1.0800000000000001E-2,74.099999999999994,78.7,239.9,2196,80.099999999999994,null,null,0.22]
[89,467.9,148,6.71,74.7,"2009-02-23T13:32:47",78.8,467.9,14.8,671,6.01,1.12E-2,74.7,79.400000000000006,237.9,2267,78.8,null,null,0.22]
[89.5,472.6,150,7.09,73.8,"2009-02-23T13:33:17",77.2,472.6,15,709,5.83,1.2200000000000001E-2,73.8,78.400000000000006,248.5,2471,77.2,null,null,0.22]
[90,488.1,152,7.17,72.599999999999994,"2009-02-23T13:33:47",78.900000000000006,488.1,15.2,717,5.65,1.2699999999999999E-2,72.599999999999994,77.099999999999994,259,2574,78.900000000000006,null,null,0.23]
[90.5,449.9,164,9.08,69.5,"2009-02-23T13:34:17",78.8,449.9,16.399999999999999,908,4.49,2.0199999999999999E-2,69.5,73.8,352.5,4109,78.8,null,null,0.15]
[91,425,155,15.1,73.7,"2009-02-23T13:34:47",77.8,425,15.5,1510,5.29,2.8500000000000001E-2,73.7,78.3,283.7,5794,77.8,null,null,0.17]
[91.5,425.9,125,45.87,78.599999999999994,"2009-02-23T13:35:17",76.8,425.9,12.5,4587,8.2100000000000009,5.5899999999999998E-2,78.599999999999994,83.4,147.30000000000001,11344,76.8,null,null,0.19]
[92,435.3,118,48.63,79.099999999999994,"2009-02-23T13:35:47",75.7,435.3,11.8,4863,8.85,5.5E-2,79.099999999999994,84,129.4,11158,75.7,null,null,0.24]
[92.5,445.3,116,55,78.8,"2009-02-23T13:36:17",76.099999999999994,445.3,11.6,5500,9.1,6.0400000000000002E-2,78.8,83.7,123.1,12270,76.099999999999994,null,null,0.21]
[93,449.2,117,50,78.8,"2009-02-23T13:36:47",76.3,449.2,11.7,5000,9.02,5.5399999999999998E-2,78.8,83.7,125.1,11253,76.3,null,null,0.21]
[93.5,448,115,50,79.099999999999994,"2009-02-23T13:37:17",75.400000000000006,448,11.5,5000,9.18,5.4399999999999997E-2,79.099999999999994,84,121.1,11053,75.400000000000006,null,null,0.2]
[94,447.4,118,50,78.599999999999994,"2009-02-23T13:37:47",75,447.4,11.8,5000,8.85,5.6500000000000002E-2,78.599999999999994,83.4,129.5,11474,75,null,null,0.2]
[94.5,454.6,121,27.07,79.2,"2009-02-23T13:38:17",75.5,454.6,12.1,2707,8.59,3.15E-2,79.2,84.1,136.19999999999999,6394,75.5,null,null,0.15]
[95,462.3,123,20.21,79.2,"2009-02-23T13:38:47",77.900000000000006,462.3,12.3,2021,8.44,2.3900000000000001E-2,79.2,84.1,140.5,4860,77.900000000000006,null,null,0.16]
[95.5,471,125,14.64,78.900000000000006,"2009-02-23T13:39:17",78.900000000000006,471,12.5,1464,8.17,1.7899999999999999E-2,78.900000000000006,83.7,148.5,3638,78.900000000000006,null,null,0.17]
[96,{"$f":"FT","v":487.3},{"$f":"Oxy*10","v":132},{"$f":"CO/100","v":13.89},{"$f":"Effg","v":77.2},"2009-02-23T13:39:47",77.900000000000006,487.3,13.2,1389,7.57,1.83E-2,77.2,81.900000000000006,168,3722,77.900000000000006,null,null,0.17]
[96.5,483.6,134,12.46,76.8,"2009-02-23T13:40:17",73.2,483.6,13.4,1246,7.39,1.6899999999999998E-2,76.8,81.599999999999994,174.9,3425,73.2,null,null,0.17]
[97,468.4,136,9.11,77.3,"2009-02-23T13:40:47",76.5,468.4,13.6,911,7.13,1.2800000000000001E-2,77.3,82,184.7,2594,76.5,null,null,0.17]
[97.5,473.4,139,8.0399999999999991,76.5,"2009-02-23T13:41:17",75.5,473.4,13.9,804,6.85,1.17E-2,76.5,81.2,196.3,2382,75.5,null,null,0.17]
[98,474,144,8.92,75,"2009-02-23T13:41:47",73.3,474,14.4,892,6.35,1.41E-2,75,79.599999999999994,219.9,2853,73.3,null,null,0.17]
[98.5,464.4,144,9.2200000000000006,75.5,"2009-02-23T13:42:17",76,464.4,14.4,922,6.34,1.4500000000000001E-2,75.5,80.2,220,2951,76,null,null,0.17]
[99,468.7,145,9.42,75.2,"2009-02-23T13:42:47",76.7,468.7,14.5,942,6.29,1.4999999999999999E-2,75.2,79.8,222.8,3040,76.7,null,null,0.17]
[99.5,471.7,149,10.29,73.900000000000006,"2009-02-23T13:43:17",77.3,471.7,14.9,1029,5.91,1.7399999999999999E-2,73.900000000000006,78.400000000000006,243.4,3533,77.3,null,null,0.17]
[100,468.2,151,10.85,73.400000000000006,"2009-02-23T13:43:47",76.8,468.2,15.1,1085,5.72,1.9E-2,73.400000000000006,77.900000000000006,254.7,3848,76.8,null,null,0.18]
[100.5,470.6,151,10.89,73.3,"2009-02-23T13:44:17",78.2,470.6,15.1,1089,5.71,1.9099999999999999E-2,73.3,77.8,255.6,3872,78.2,null,null,0.18]
[101,462.3,152,11.2,73.400000000000006,"2009-02-23T13:44:47",78.5,462.3,15.2,1120,5.64,1.9800000000000002E-2,73.400000000000006,78,259.7,4029,78.5,null,null,0.18]
[101.5,464.8,153,12.17,72.5,"2009-02-23T13:45:17",77.599999999999994,464.8,15.3,1217,5.46,2.23E-2,72.5,77,271.60000000000002,4523,77.599999999999994,null,null,0.18]
[102,461.7,156,13.49,71.7,"2009-02-23T13:45:47",77.400000000000006,461.7,15.6,1349,5.23,2.58E-2,71.7,76.099999999999994,288.39999999999998,5240,77.400000000000006,null,null,0.18]
[102.5,464.7,156,16.510000000000002,71.099999999999994,"2009-02-23T13:46:17",77.900000000000006,464.7,15.6,1651,5.18,3.1800000000000002E-2,71.099999999999994,75.5,291.60000000000002,6465,77.900000000000006,null,null,0.18]
[103,460.7,158,16.87,70.8,"2009-02-23T13:46:47",78.099999999999994,460.7,15.8,1687,5.07,3.3300000000000003E-2,70.8,75.099999999999994,300.60000000000002,6758,78.099999999999994,null,null,0.18]
[103.5,463.9,160,18.809999999999999,69.599999999999994,"2009-02-23T13:47:17",79.099999999999994,463.9,16,1881,4.88,3.8600000000000002E-2,69.599999999999994,73.900000000000006,316.3,7830,79.099999999999994,null,null,0.19]
[104,458.1,161,22.3,68.900000000000006,"2009-02-23T13:47:47",80.7,458.1,16.100000000000001,2230,4.72,4.7300000000000002E-2,68.900000000000006,73.2,330.2,9594,80.7,null,null,0.19]
[104.5,461.6,164,22.2,67.3,"2009-02-23T13:48:17",79.8,461.6,16.399999999999999,2220,4.47,4.9700000000000001E-2,67.3,71.5,354.4,10087,79.8,null,null,0.19]
[105,458.5,166,21.12,66.599999999999994,"2009-02-23T13:48:47",79.099999999999994,458.5,16.600000000000001,2112,4.3,4.9099999999999998E-2,66.599999999999994,70.7,372.2,9973,79.099999999999994,null,null,0.19]
[105.5,454.3,167,21.24,66,"2009-02-23T13:49:17",79.7,454.3,16.7,2124,4.16,5.11E-2,66,70.099999999999994,388.5,10375,79.7,null,null,0.19]
[106,464.6,168,21.95,64.599999999999994,"2009-02-23T13:49:47",80.5,464.6,16.8,2195,4.05,5.4199999999999998E-2,64.599999999999994,68.599999999999994,401.6,11010,80.5,null,null,0.2]
[106.5,457.8,168,22.38,64.900000000000006,"2009-02-23T13:50:17",80.099999999999994,457.8,16.8,2238,4.04,5.5399999999999998E-2,64.900000000000006,68.900000000000006,402.3,11242,80.099999999999994,null,null,0.2]
[107,455.8,170,23.43,64,"2009-02-23T13:50:47",80,455.8,17,2343,3.91,0.06,64,67.900000000000006,419.8,12179,80,null,null,0.2]
[107.5,453.8,171,24.18,63.3,"2009-02-23T13:51:17",80,453.8,17.100000000000001,2418,3.81,6.3500000000000001E-2,63.3,67.2,433,12889,80,null,null,0.22]
[108,448.1,171,24.5,63,"2009-02-23T13:51:47",77.900000000000006,448.1,17.100000000000001,2450,3.74,6.54E-2,63,66.900000000000006,442.2,13285,77.900000000000006,null,null,0.22]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.8,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,59.3,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,59,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,61,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.3,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60.8,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.5,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.400000000000006,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.400000000000006,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.599999999999994,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.8,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.2,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.099999999999994,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.7,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.099999999999994,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.8,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.2,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,61.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.1,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.900000000000006,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.8,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.599999999999994,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.599999999999994,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.400000000000006,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.900000000000006,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.400000000000006,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,66,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,null,null,0.4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]