{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Online"],"not_rendered":{"charts":1,"images":0,"macros":0,"external_links":0,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Online","index":0,"n_rows":283,"n_cols":20,"rows_kept":283,"cut":false,"hidden":false,"merged":[]}
["Minutes","°F FT","% O2x10","% COx100","% Effg","Date / time","°F AT","°F FT","% O2","ppm CO","% CO2","ratio","% Effg","% Effn","% ExAir","ppm uCO","°F AT","ppm amCO2","ppm amCO","l/min Pump"]
[null,{"$f":"AVERAGE(FT)","v":329.66682464454971},{"$f":"AVERAGE(Oxy)","v":12.504739336492891},{"$f":"AVERAGE(CO)","v":911.62085308056874},{"$f":"AVERAGE(Effg)","v":84.015533980582489}]
[]
[]
[]
[1.5,{"$f":"FT","v":107.4},{"$f":"Oxy*10","v":210},{"$f":"CO/100","v":0.23},{"$f":"Effg","v":0},"2009-02-11T09:45:06",67.900000000000006,107.4,21,23,null,null,null,null,null,null,67.900000000000006,null,null,0.56999999999999995]
[2,108.7,208,3.74,0,"2009-02-11T09:45:38",68.099999999999994,108.7,20.8,374,null,null,null,null,null,null,68.099999999999994,null,null,0.56000000000000005]
[2.5,109.6,206,6.05,0,"2009-02-11T09:46:10",68.599999999999994,109.6,20.6,605,null,null,null,null,null,null,68.599999999999994,null,null,0.55000000000000004]
[3,110.5,206,7.88,0,"2009-02-11T09:46:42",68.7,110.5,20.6,788,null,null,null,null,null,null,68.7,null,null,0.5]
[3.5,118.2,201,14.5,0,"2009-02-11T09:47:14",68.8,118.2,20.100000000000001,1450,null,null,null,null,null,null,68.8,null,null,0.38]
[4,124.1,191,30.27,78.3,"2009-02-11T09:47:46",68.8,124.1,19.100000000000001,3027,1.87,0.16170000000000001,78.3,83.1,984.2,32818,68.8,null,null,0.28999999999999998]
[4.5,136.1,180,32.85,81.8,"2009-02-11T09:48:18",68.8,136.1,18,3285,2.86,0.115,81.8,86.8,610.5,23341,68.8,null,null,0.26]
[5,145.5,160,29,86.3,"2009-02-11T09:48:50",69,145.5,16,2900,4.84,5.9900000000000002E-2,86.3,91.6,319.60000000000002,12169,69,null,null,0.3]
[5.5,159.80000000000001,136,25.61,88.2,"2009-02-11T09:49:22",69,159.80000000000001,13.6,2561,7.16,3.5799999999999998E-2,88.2,93.7,183.6,7264,69,null,null,0.2]
[6,173.6,116,44.1,87.9,"2009-02-11T09:49:54",68.3,173.6,11.6,4410,9.1199999999999992,4.8399999999999999E-2,87.9,93.3,122.6,9816,68.3,null,null,0.17]
[6.5,178.1,106,75,86.8,"2009-02-11T09:50:26",68.7,178.1,10.6,7500,10.029999999999999,7.4700000000000003E-2,86.8,92.2,102.3,15174,68.7,null,null,0.17]
[7,195.3,103,50,87.6,"2009-02-11T09:50:58",68.7,195.3,10.3,5000,10.3,4.8599999999999997E-2,87.6,93,97.1,9857,68.7,null,null,0.15]
[7.5,193.8,102,50,87.7,"2009-02-11T09:51:30",69.3,193.8,10.199999999999999,5000,10.41,4.8000000000000001E-2,87.7,93.2,94.9,9747,69.3,null,null,0.15]
[8,199.3,100,50,87.7,"2009-02-11T09:52:02",69.400000000000006,199.3,10,5000,10.63,4.7E-2,87.7,93.1,91,9549,69.400000000000006,null,null,0.15]
[8.5,206.1,99,50,87.5,"2009-02-11T09:52:34",69.599999999999994,206.1,9.9,5000,10.69,4.6800000000000001E-2,87.5,93,89.9,9493,69.599999999999994,null,null,0.15]
[9,211.2,137,63.85,83.5,"2009-02-11T09:53:06",69.599999999999994,211.2,13.7,6385,7.02,9.0899999999999995E-2,83.5,88.7,189.1,18460,69.599999999999994,null,null,0.56000000000000005]
[9.5,206.2,107,50,87.1,"2009-02-11T09:53:38",69.599999999999994,206.2,10.7,5000,9.92,5.04E-2,87.1,92.5,104.6,10230,69.599999999999994,null,null,0.56999999999999995]
[10,212.6,108,50,86.9,"2009-02-11T09:54:10",69.5,212.6,10.8,5000,9.86,5.0700000000000002E-2,86.9,92.3,105.9,10296,69.5,null,null,0.56000000000000005]
[10.5,212.5,108,50,86.9,"2009-02-11T09:54:42",69.599999999999994,212.5,10.8,5000,9.9,5.0500000000000003E-2,86.9,92.3,105,10251,69.599999999999994,null,null,0.56000000000000005]
[11,215.2,109,50,86.8,"2009-02-11T09:55:14",70,215.2,10.9,5000,9.81,5.0999999999999997E-2,86.8,92.1,107,10350,70,null,null,0.55000000000000004]
[11.5,213.1,112,16.73,88.3,"2009-02-11T09:55:46",69.5,213.1,11.2,1673,9.43,1.77E-2,88.3,93.8,115.2,3600,69.5,null,null,0.52]
[12,217.2,118,9.39,88.3,"2009-02-11T09:56:18",70.099999999999994,217.2,11.8,939,8.92,1.0500000000000001E-2,88.3,93.8,127.5,2136,70.099999999999994,null,null,0.52]
[12.5,215.7,123,6.62,88.3,"2009-02-11T09:56:50",70.400000000000006,215.7,12.3,662,8.42,7.9000000000000008E-3,88.3,93.8,141,1595,70.400000000000006,null,null,0.52]
[13,211.2,127,5.27,88.3,"2009-02-11T09:57:22",70.3,211.2,12.7,527,8.0500000000000007,6.4999999999999997E-3,88.3,93.8,152.19999999999999,1329,70.3,null,null,0.53]
[13.5,211.8,129,4.62,88.2,"2009-02-11T09:57:54",70.900000000000006,211.8,12.9,462,7.8,5.8999999999999999E-3,88.2,93.6,160.19999999999999,1202,70.900000000000006,null,null,0.52]
[14,214.1,130,3.86,88,"2009-02-11T09:58:26",70.099999999999994,214.1,13,386,7.69,5.0000000000000001E-3,88,93.5,164,1019,70.099999999999994,null,null,0.52]
[14.5,220.8,131,3.42,87.8,"2009-02-11T09:58:58",70.599999999999994,220.8,13.1,342,7.59,4.4999999999999997E-3,87.8,93.2,167.4,915,70.599999999999994,null,null,0.52]
[15,223.9,133,3.37,87.5,"2009-02-11T09:59:30",70.5,223.9,13.3,337,7.45,4.4999999999999997E-3,87.5,93,172.4,918,70.5,null,null,0.52]
[15.5,224.7,134,3.5,87.4,"2009-02-11T10:00:02",70.599999999999994,224.7,13.4,350,7.35,4.7999999999999996E-3,87.4,92.8,176.3,967,70.599999999999994,null,null,0.53]
[16,224.2,131,4.87,87.6,"2009-02-11T10:00:34",70.599999999999994,224.2,13.1,487,7.65,6.4000000000000003E-3,87.6,93,165.3,1292,70.599999999999994,null,null,0.53]
[16.5,224.1,131,5.82,87.5,"2009-02-11T10:01:06",70.599999999999994,224.1,13.1,582,7.63,7.6E-3,87.5,92.9,166.2,1549,70.599999999999994,null,null,0.52]
[17,231.7,132,5.77,87.1,"2009-02-11T10:01:38",70.099999999999994,231.7,13.2,577,7.53,7.7000000000000002E-3,87.1,92.5,169.6,1556,70.099999999999994,null,null,0.51]
[17.5,226.4,132,5.05,87.4,"2009-02-11T10:02:10",70.2,226.4,13.2,505,7.5,6.7000000000000002E-3,87.4,92.8,170.7,1367,70.2,null,null,0.5]
[18,234.2,131,4.79,87.2,"2009-02-11T10:02:42",70.099999999999994,234.2,13.1,479,7.67,6.1999999999999998E-3,87.2,92.6,164.5,1267,70.099999999999994,null,null,0.49]
[18.5,229.3,134,4.3099999999999996,87.1,"2009-02-11T10:03:14",70.2,229.3,13.4,431,7.31,5.8999999999999999E-3,87.1,92.5,177.7,1197,70.2,null,null,0.49]
[19,231.6,135,4.88,86.9,"2009-02-11T10:03:46",69.5,231.6,13.5,488,7.27,6.7000000000000002E-3,86.9,92.3,179.2,1362,69.5,null,null,0.5]
[19.5,232.4,132,4.49,87.2,"2009-02-11T10:04:18",70.2,232.4,13.2,449,7.52,6.0000000000000001E-3,87.2,92.6,170.1,1213,70.2,null,null,0.49]
[20,236.5,132,3.5,87.1,"2009-02-11T10:04:50",70,236.5,13.2,350,7.51,4.7000000000000002E-3,87.1,92.5,170.4,946,70,null,null,0.48]
[20.5,234.9,133,4.83,86.9,"2009-02-11T10:05:22",69.400000000000006,234.9,13.3,483,7.41,6.4999999999999997E-3,86.9,92.3,173.8,1322,69.400000000000006,null,null,0.48]
[21,238.4,136,6.51,86.4,"2009-02-11T10:05:54",69.400000000000006,238.4,13.6,651,7.12,9.1000000000000004E-3,86.4,91.8,185.1,1856,69.400000000000006,null,null,0.48]
[21.5,236.3,137,6.97,86.4,"2009-02-11T10:06:26",69.2,236.3,13.7,697,7.05,9.9000000000000008E-3,86.4,91.7,187.9,2006,69.2,null,null,0.49]
[22,235.2,135,8.9,86.5,"2009-02-11T10:06:58",69.599999999999994,235.2,13.5,890,7.22,1.23E-2,86.5,91.8,181.3,2504,69.599999999999994,null,null,0.48]
[22.5,238.8,139,8.82,85.9,"2009-02-11T10:07:30",69.5,238.8,13.9,882,6.83,1.29E-2,85.9,91.3,197.2,2622,69.5,null,null,0.47]
[23,232.9,144,10.64,85.6,"2009-02-11T10:08:02",69.8,232.9,14.4,1064,6.41,1.66E-2,85.6,90.9,216.6,3369,69.8,null,null,0.45]
[23.5,234.1,144,10.220000000000001,85.5,"2009-02-11T10:08:34",69.7,234.1,14.4,1022,6.39,1.6E-2,85.5,90.8,217.7,3247,69.7,null,null,0.44]
[24,246.3,138,5.92,86,"2009-02-11T10:09:06",70.2,246.3,13.8,592,6.98,8.5000000000000006E-3,86,91.4,190.7,1721,70.2,null,null,0.42]
[24.5,249.5,133,4.26,86.5,"2009-02-11T10:09:38",70.2,249.5,13.3,426,7.48,5.7000000000000002E-3,86.5,91.9,171.3,1156,70.2,null,null,0.42]
[25,245.7,133,3.91,86.7,"2009-02-11T10:10:10",70.400000000000006,245.7,13.3,391,7.49,5.1999999999999998E-3,86.7,92.1,171.1,1060,70.400000000000006,null,null,0.41]
[25.5,250.1,129,4.16,86.8,"2009-02-11T10:10:42",70.900000000000006,250.1,12.9,416,7.85,5.3E-3,86.8,92.2,158.5,1075,70.900000000000006,null,null,0.39]
[26,246.8,133,4.17,86.6,"2009-02-11T10:11:14",70.900000000000006,246.8,13.3,417,7.46,5.5999999999999999E-3,86.6,92,172.1,1135,70.900000000000006,null,null,0.36]
[26.5,246.3,135,4.55,86.4,"2009-02-11T10:11:46",70.8,246.3,13.5,455,7.25,6.3E-3,86.4,91.8,180.1,1274,70.8,null,null,0.33]
[27,249.2,131,4.04,86.7,"2009-02-11T10:12:18",70.2,249.2,13.1,404,7.66,5.3E-3,86.7,92.1,165,1071,70.2,null,null,0.31]
[27.5,247.4,128,3.97,87,"2009-02-11T10:12:50",71.099999999999994,247.4,12.8,397,7.91,5.0000000000000001E-3,87,92.4,156.6,1019,71.099999999999994,null,null,0.3]
[28,253.9,129,3.94,86.7,"2009-02-11T10:13:22",71.3,253.9,12.9,394,7.83,5.0000000000000001E-3,86.7,92.1,159.4,1022,71.3,null,null,0.28000000000000003]
[28.5,261.7,128,3.88,86.5,"2009-02-11T10:13:54",70.3,261.7,12.8,388,7.93,4.8999999999999998E-3,86.5,91.8,155.9,993,70.3,null,null,0.27]
[29,262.3,128,3.98,86.5,"2009-02-11T10:14:26",71.2,262.3,12.8,398,7.94,5.0000000000000001E-3,86.5,91.8,155.5,1017,71.2,null,null,0.23]
[29.5,258.5,129,3.6,86.5,"2009-02-11T10:14:58",70.7,258.5,12.9,360,7.82,4.5999999999999999E-3,86.5,91.9,159.6,934,70.7,null,null,0.22]
[30,255,126,3.29,86.9,"2009-02-11T10:15:30",71.2,255,12.6,329,8.09,4.1000000000000003E-3,86.9,92.3,150.80000000000001,825,71.2,null,null,0.19]
[30.5,270.2,122,2.84,86.7,"2009-02-11T10:16:02",71.2,270.2,12.2,284,8.5399999999999991,3.3E-3,86.7,92.1,137.69999999999999,675,71.2,null,null,0.15]
[31,269.5,115,4.22,87.2,"2009-02-11T10:16:34",71.8,269.5,11.5,422,9.23,4.5999999999999999E-3,87.2,92.6,120.1,929,71.8,null,null,0.13]
[31.5,279.10000000000002,110,6.53,87,"2009-02-11T10:17:06",71.7,279.10000000000002,11,653,9.65,6.7999999999999996E-3,87,92.4,110.3,1373,71.7,null,null,0.13]
[32,{"$f":"FT","v":284.60000000000002},{"$f":"Oxy*10","v":107},{"$f":"CO/100","v":9.64},{"$f":"Effg","v":86.9},"2009-02-11T10:17:38",71.5,284.60000000000002,10.7,964,9.91,9.7000000000000003E-3,86.9,92.2,104.8,1975,71.5,null,null,0.11]
[32.5,284.39999999999998,106,10.8,86.9,"2009-02-11T10:18:10",70.900000000000006,284.39999999999998,10.6,1080,10.029999999999999,1.0800000000000001E-2,86.9,92.2,102.4,2185,70.900000000000006,null,null,0.11]
[33,289.39999999999998,106,18.41,86.3,"2009-02-11T10:18:42",70.7,289.39999999999998,10.6,1841,10.06,1.83E-2,86.3,91.7,101.9,3717,70.7,null,null,0.13]
[33.5,293.10000000000002,101,35.53,85.7,"2009-02-11T10:19:14",71.3,293.10000000000002,10.1,3553,10.51,3.3799999999999997E-2,85.7,91,93.1,6860,71.3,null,null,0.1]
[34,299.2,93,150,81.400000000000006,"2009-02-11T10:19:46",71,299.2,9.3000000000000007,15000,11.28,0.13300000000000001,81.400000000000006,86.5,80,27003,71,null,null,0.13]
[34.5,294.89999999999998,97,19.96,86.6,"2009-02-11T10:20:18",70.8,294.89999999999998,9.6999999999999993,1996,10.88,1.84E-2,86.6,92,86.6,3725,70.8,null,null,0.09]
[35,309.5,104,15.41,86,"2009-02-11T10:20:50",70.900000000000006,309.5,10.4,1541,10.27,1.4999999999999999E-2,86,91.4,97.7,3047,70.900000000000006,null,null,0.09]
[35.5,301.89999999999998,107,11.68,86.2,"2009-02-11T10:21:22",69.8,301.89999999999998,10.7,1168,9.99,1.17E-2,86.2,91.6,103.1,2372,69.8,null,null,0.09]
[36,297.2,157,3.55,81,"2009-02-11T10:21:54",71.2,297.2,15.7,355,5.16,6.8999999999999999E-3,81,86,293.60000000000002,1397,71.2,null,null,0.61]
[36.5,307.2,114,6.05,85.9,"2009-02-11T10:22:26",71.099999999999994,307.2,11.4,605,9.24,6.4999999999999997E-3,85.9,91.2,119.7,1329,71.099999999999994,null,null,0.61]
[37,312,114,4.5,85.8,"2009-02-11T10:22:58",71.099999999999994,312,11.4,450,9.2799999999999994,4.7999999999999996E-3,85.8,91.2,118.7,984,71.099999999999994,null,null,0.6]
[37.5,320.5,114,2.66,85.7,"2009-02-11T10:23:30",71.900000000000006,320.5,11.4,266,9.3000000000000007,2.8999999999999998E-3,85.7,91,118.2,580,71.900000000000006,null,null,0.61]
[38,332.9,109,2.46,85.6,"2009-02-11T10:24:02",71.099999999999994,332.9,10.9,246,9.7200000000000006,2.5000000000000001E-3,85.6,90.9,108.9,514,71.099999999999994,null,null,0.6]
[38.5,322.89999999999998,109,2.4500000000000002,86,"2009-02-11T10:24:34",71.2,322.89999999999998,10.9,245,9.75,2.5000000000000001E-3,86,91.3,108.3,510,71.2,null,null,0.6]
[39,338.2,110,2,85.5,"2009-02-11T10:25:06",71.099999999999994,338.2,11,200,9.7100000000000009,2.0999999999999999E-3,85.5,90.8,109.2,418,71.099999999999994,null,null,0.6]
[39.5,332.4,111,1.65,85.6,"2009-02-11T10:25:38",71.5,332.4,11.1,165,9.6199999999999992,1.6999999999999999E-3,85.6,90.9,111.1,348,71.5,null,null,0.6]
[40,331.9,109,1.83,85.8,"2009-02-11T10:26:10",72.599999999999994,331.9,10.9,183,9.77,1.9E-3,85.8,91.1,107.8,380,72.599999999999994,null,null,0.59]
[40.5,339.2,110,2.23,85.5,"2009-02-11T10:26:42",73.099999999999994,339.2,11,223,9.6999999999999993,2.3E-3,85.5,90.8,109.3,467,73.099999999999994,null,null,0.59]
[41,334.9,109,2.64,85.7,"2009-02-11T10:27:14",73.7,334.9,10.9,264,9.8000000000000007,2.7000000000000001E-3,85.7,91,107.1,547,73.7,null,null,0.59]
[41.5,338.4,111,2.02,85.4,"2009-02-11T10:27:46",73.5,338.4,11.1,202,9.56,2.0999999999999999E-3,85.4,90.7,112.3,429,73.5,null,null,0.59]
[42,340.7,111,2.1800000000000002,85.4,"2009-02-11T10:28:18",74.3,340.7,11.1,218,9.61,2.3E-3,85.4,90.7,111.2,460,74.3,null,null,0.59]
[42.5,347.4,113,2.0099999999999998,85.1,"2009-02-11T10:28:50",74.7,347.4,11.3,201,9.39,2.0999999999999999E-3,85.1,90.3,116.1,434,74.7,null,null,0.6]
[43,354.5,112,2.17,84.9,"2009-02-11T10:29:22",74.3,354.5,11.2,217,9.4600000000000009,2.3E-3,84.9,90.1,114.6,466,74.3,null,null,0.6]
[43.5,354.7,114,1.88,84.8,"2009-02-11T10:29:54",74.3,354.7,11.4,188,9.31,2E-3,84.8,90,118.1,410,74.3,null,null,0.6]
[44,351.5,111,1.92,85,"2009-02-11T10:30:26",72.599999999999994,351.5,11.1,192,9.5299999999999994,2E-3,85,90.3,113,409,72.599999999999994,null,null,0.6]
[44.5,360.7,112,1.88,84.6,"2009-02-11T10:30:58",72.5,360.7,11.2,188,9.43,2E-3,84.6,89.9,115.2,405,72.5,null,null,0.6]
[45,351,109,2.17,85.2,"2009-02-11T10:31:30",73.900000000000006,351,10.9,217,9.7799999999999994,2.2000000000000001E-3,85.2,90.5,107.5,450,73.900000000000006,null,null,0.61]
[45.5,354.4,110,2.2400000000000002,85.1,"2009-02-11T10:32:02",74.5,354.4,11,224,9.69,2.3E-3,85.1,90.4,109.6,469,74.5,null,null,0.6]
[46,353.3,110,2.27,85,"2009-02-11T10:32:34",73.900000000000006,353.3,11,227,9.6199999999999992,2.3999999999999998E-3,85,90.3,111,479,73.900000000000006,null,null,0.6]
[46.5,358.6,106,8.09,85,"2009-02-11T10:33:06",75.400000000000006,358.6,10.6,809,10.09,8.0000000000000002E-3,85,90.3,101.1,1627,75.400000000000006,null,null,0.61]
[47,356.4,105,7.6,85.1,"2009-02-11T10:33:38",75.5,356.4,10.5,760,10.15,7.4999999999999997E-3,85.1,90.4,99.9,1520,75.5,null,null,0.63]
[47.5,357.7,107,7.21,85,"2009-02-11T10:34:10",75.7,357.7,10.7,721,9.99,7.1999999999999998E-3,85,90.3,103.2,1465,75.7,null,null,0.63]
[48,365.8,107,5.93,84.8,"2009-02-11T10:34:42",75.400000000000006,365.8,10.7,593,9.92,6.0000000000000001E-3,84.8,90,104.6,1213,75.400000000000006,null,null,0.63]
[48.5,366.8,109,4.3499999999999996,84.7,"2009-02-11T10:35:14",75.599999999999994,366.8,10.9,435,9.81,4.4000000000000003E-3,84.7,90,106.9,900,75.599999999999994,null,null,0.62]
[49,354.2,110,4.08,85.1,"2009-02-11T10:35:46",76.400000000000006,354.2,11,408,9.6999999999999993,4.1999999999999997E-3,85.1,90.3,109.3,854,76.400000000000006,null,null,0.62]
[49.5,358.9,110,3.16,84.8,"2009-02-11T10:36:18",73.3,358.9,11,316,9.64,3.3E-3,84.8,90.1,110.7,666,73.3,null,null,0.62]
[50,360.8,113,2.81,84.5,"2009-02-11T10:36:50",72.2,360.8,11.3,281,9.39,3.0000000000000001E-3,84.5,89.8,116.2,608,72.2,null,null,0.62]
[50.5,367.7,116,2.48,84.1,"2009-02-11T10:37:22",74.400000000000006,367.7,11.6,248,9.1199999999999992,2.7000000000000001E-3,84.1,89.4,122.7,552,74.400000000000006,null,null,0.62]
[51,368.8,119,2.2999999999999998,83.9,"2009-02-11T10:37:54",75,368.8,11.9,230,8.83,2.5999999999999999E-3,83.9,89,129.9,529,75,null,null,0.61]
[51.5,369.6,119,2.2599999999999998,83.8,"2009-02-11T10:38:26",75.7,369.6,11.9,226,8.8000000000000007,2.5999999999999999E-3,83.8,89,130.6,521,75.7,null,null,0.61]
[52,369.7,120,1.96,83.7,"2009-02-11T10:38:58",75.099999999999994,369.7,12,196,8.67,2.3E-3,83.7,88.9,134,459,75.099999999999994,null,null,0.61]
[52.5,377.2,121,2.08,83.3,"2009-02-11T10:39:30",74.900000000000006,377.2,12.1,208,8.58,2.3999999999999998E-3,83.3,88.5,136.5,492,74.900000000000006,null,null,0.61]
[53,367.3,121,1.89,83.7,"2009-02-11T10:40:02",75.3,367.3,12.1,189,8.6,2.2000000000000001E-3,83.7,88.9,136.1,446,75.3,null,null,0.62]
[53.5,360.9,120,1.79,84.1,"2009-02-11T10:40:34",76,360.9,12,179,8.6999999999999993,2.0999999999999999E-3,84.1,89.3,133.30000000000001,418,76,null,null,0.61]
[54,370.7,119,1.71,83.8,"2009-02-11T10:41:06",76.099999999999994,370.7,11.9,171,8.76,2E-3,83.8,89,131.80000000000001,396,76.099999999999994,null,null,0.61]
[54.5,377.7,115,1.38,84,"2009-02-11T10:41:38",76.400000000000006,377.7,11.5,138,9.17,1.5E-3,84,89.2,121.3,305,76.400000000000006,null,null,0.61]
[55,373.8,113,1.41,84.4,"2009-02-11T10:42:10",77,373.8,11.3,141,9.39,1.5E-3,84.4,89.6,116.2,305,77,null,null,0.6]
[55.5,375.8,114,1.34,84.2,"2009-02-11T10:42:42",76.599999999999994,375.8,11.4,134,9.32,1.4E-3,84.2,89.4,117.9,292,76.599999999999994,null,null,0.6]
[56,374.6,117,1.51,83.8,"2009-02-11T10:43:14",73.3,374.6,11.7,151,9.0299999999999994,1.6999999999999999E-3,83.8,89,124.9,340,73.3,null,null,0.59]
[56.5,384.7,116,1.36,83.6,"2009-02-11T10:43:46",72.099999999999994,384.7,11.6,136,9.11,1.5E-3,83.6,88.8,122.8,303,72.099999999999994,null,null,0.6]
[57,382.6,117,1.21,83.5,"2009-02-11T10:44:18",71.7,382.6,11.7,121,8.9499999999999993,1.4E-3,83.5,88.6,126.9,275,71.7,null,null,0.59]
[57.5,385.1,119,1.19,83.3,"2009-02-11T10:44:50",72.400000000000006,385.1,11.9,119,8.83,1.2999999999999999E-3,83.3,88.4,129.9,274,72.400000000000006,null,null,0.57999999999999996]
[58,378.1,121,1.24,83.3,"2009-02-11T10:45:22",72.8,378.1,12.1,124,8.61,1.4E-3,83.3,88.5,135.9,292,72.8,null,null,0.57999999999999996]
[58.5,382.6,121,1.27,83,"2009-02-11T10:45:54",72.099999999999994,382.6,12.1,127,8.56,1.5E-3,83,88.2,137.30000000000001,301,72.099999999999994,null,null,0.59]
[59,392.2,121,1.32,82.8,"2009-02-11T10:46:26",71.8,392.2,12.1,132,8.64,1.5E-3,82.8,87.9,135,310,71.8,null,null,0.57999999999999996]
[59.5,389.9,122,1.36,82.8,"2009-02-11T10:46:58",73.400000000000006,389.9,12.2,136,8.5,1.6000000000000001E-3,82.8,87.9,138.9,325,73.400000000000006,null,null,0.57999999999999996]
[60,381.3,123,1.27,82.9,"2009-02-11T10:47:30",72,381.3,12.3,127,8.42,1.5E-3,82.9,88.1,141,306,72,null,null,0.59]
[60.5,384.1,122,1.63,83,"2009-02-11T10:48:02",73,384.1,12.2,163,8.5,1.9E-3,83,88.1,138.80000000000001,389,73,null,null,0.57999999999999996]
[61,388.2,121,1.56,83,"2009-02-11T10:48:34",73.8,388.2,12.1,156,8.65,1.8E-3,83,88.2,134.69999999999999,366,73.8,null,null,0.56999999999999995]
[61.5,384.9,119,1.55,83.3,"2009-02-11T10:49:06",74.2,384.9,11.9,155,8.76,1.8E-3,83.3,88.4,131.9,359,74.2,null,null,0.55000000000000004]
[62,390,119,1.74,83.1,"2009-02-11T10:49:38",75.5,390,11.9,174,8.77,2E-3,83.1,88.3,131.6,403,75.5,null,null,0.56000000000000005]
[62.5,385,121,1.51,83.1,"2009-02-11T10:50:10",74.7,385,12.1,151,8.57,1.8E-3,83.1,88.2,137,358,74.7,null,null,0.55000000000000004]
[63,390.9,121,1.53,82.8,"2009-02-11T10:50:42",71.8,390.9,12.1,153,8.6300000000000008,1.8E-3,82.8,88,135.19999999999999,360,71.8,null,null,0.56000000000000005]
[63.5,389.7,119,1.46,83,"2009-02-11T10:51:14",70.599999999999994,389.7,11.9,146,8.77,1.6999999999999999E-3,83,88.1,131.5,338,70.599999999999994,null,null,0.56000000000000005]
[64,{"$f":"FT","v":385.5},{"$f":"Oxy*10","v":120},{"$f":"CO/100","v":1.57},{"$f":"Effg","v":83.1},"2009-02-11T10:51:46",72,385.5,12,157,8.73,1.8E-3,83.1,88.3,132.6,365,72,null,null,0.56999999999999995]
[64.5,383.9,119,1.65,83.3,"2009-02-11T10:52:18",72.400000000000006,383.9,11.9,165,8.7899999999999991,1.9E-3,83.3,88.4,130.9,381,72.400000000000006,null,null,0.56999999999999995]
[65,386.3,117,1.98,83.3,"2009-02-11T10:52:50",70.599999999999994,386.3,11.7,198,9.0299999999999994,2.2000000000000001E-3,83.3,88.5,124.8,445,70.599999999999994,null,null,0.56999999999999995]
[65.5,384,116,2.09,83.4,"2009-02-11T10:53:22",68.8,384,11.6,209,9.1,2.3E-3,83.4,88.6,123.1,466,68.8,null,null,0.56999999999999995]
[66,382,116,2.04,83.5,"2009-02-11T10:53:54",71.5,382,11.6,204,9.0500000000000007,2.3E-3,83.5,88.7,124.3,458,71.5,null,null,0.56999999999999995]
[66.5,391.1,118,2.0099999999999998,83.1,"2009-02-11T10:54:26",71.400000000000006,391.1,11.8,201,8.89,2.3E-3,83.1,88.2,128.30000000000001,459,71.400000000000006,null,null,0.56999999999999995]
[67,390.7,117,1.94,83.2,"2009-02-11T10:54:58",73.5,390.7,11.7,194,8.9600000000000009,2.2000000000000001E-3,83.2,88.4,126.5,439,73.5,null,null,0.57999999999999996]
[67.5,379.7,118,2.13,83.5,"2009-02-11T10:55:30",73,379.7,11.8,213,8.91,2.3999999999999998E-3,83.5,88.7,127.7,485,73,null,null,0.56999999999999995]
[68,384,120,2.59,83.3,"2009-02-11T10:56:02",76.3,384,12,259,8.7200000000000006,3.0000000000000001E-3,83.3,88.4,132.80000000000001,603,76.3,null,null,0.56999999999999995]
[68.5,383.2,121,2.97,83.2,"2009-02-11T10:56:34",77.3,383.2,12.1,297,8.61,3.5000000000000001E-3,83.2,88.3,135.9,701,77.3,null,null,0.56999999999999995]
[69,380.8,124,2.7,82.8,"2009-02-11T10:57:06",73.900000000000006,380.8,12.4,270,8.34,3.2000000000000002E-3,82.8,88,143.4,657,73.900000000000006,null,null,0.56999999999999995]
[69.5,388.9,125,3.1,82.4,"2009-02-11T10:57:38",73.3,388.9,12.5,310,8.24,3.8E-3,82.4,87.5,146.4,764,73.3,null,null,0.56999999999999995]
[70,382.8,125,3.26,82.7,"2009-02-11T10:58:10",76,382.8,12.5,326,8.2100000000000009,4.0000000000000001E-3,82.7,87.8,147.30000000000001,806,76,null,null,0.56999999999999995]
[70.5,379.2,126,3.28,82.6,"2009-02-11T10:58:42",73.400000000000006,379.2,12.6,328,8.14,4.0000000000000001E-3,82.6,87.7,149.4,818,73.400000000000006,null,null,0.56000000000000005]
[71,390.4,125,3.9,82.2,"2009-02-11T10:59:14",72.599999999999994,390.4,12.5,390,8.1999999999999993,4.7999999999999996E-3,82.2,87.3,147.6,966,72.599999999999994,null,null,0.56000000000000005]
[71.5,386.9,124,4.26,82.5,"2009-02-11T10:59:46",75.7,386.9,12.4,426,8.2899999999999991,5.1000000000000004E-3,82.5,87.7,144.80000000000001,1043,75.7,null,null,0.56000000000000005]
[72,393,127,5.52,82,"2009-02-11T11:00:18",77.7,393,12.7,552,8.02,6.8999999999999999E-3,82,87,153.19999999999999,1398,77.7,null,null,0.55000000000000004]
[72.5,388,126,5.76,82.2,"2009-02-11T11:00:50",76,388,12.6,576,8.09,7.1000000000000004E-3,82.2,87.2,150.9,1445,76,null,null,0.55000000000000004]
[73,382.3,127,7.84,82.1,"2009-02-11T11:01:22",77.3,382.3,12.7,784,7.99,9.7999999999999997E-3,82.1,87.2,154.1,1993,77.3,null,null,0.55000000000000004]
[73.5,393.5,127,9.6,81.7,"2009-02-11T11:01:54",76.900000000000006,393.5,12.7,960,8.06,1.1900000000000001E-2,81.7,86.8,151.80000000000001,2418,76.900000000000006,null,null,0.55000000000000004]
[74,385.4,126,7.9,82.2,"2009-02-11T11:02:26",78.400000000000006,385.4,12.6,790,8.09,9.7999999999999997E-3,82.2,87.3,151.1,1984,78.400000000000006,null,null,0.54]
[74.5,390.2,127,7.93,82,"2009-02-11T11:02:58",79.5,390.2,12.7,793,8.02,9.9000000000000008E-3,82,87.1,153.1,2007,79.5,null,null,0.54]
[75,395,124,7.24,82.2,"2009-02-11T11:03:30",79.5,395,12.4,724,8.3000000000000007,8.6999999999999994E-3,82.2,87.3,144.5,1770,79.5,null,null,0.53]
[75.5,390.3,125,6.8,82,"2009-02-11T11:04:02",72.5,390.3,12.5,680,8.18,8.3000000000000001E-3,82,87.1,148.1,1687,72.5,null,null,0.52]
[76,393.5,126,5.93,81.8,"2009-02-11T11:04:34",71.3,393.5,12.6,593,8.08,7.3000000000000001E-3,81.8,86.8,151.19999999999999,1490,71.3,null,null,0.51]
[76.5,399.1,127,5.64,81.5,"2009-02-11T11:05:06",72.2,399.1,12.7,564,8.0299999999999994,7.0000000000000001E-3,81.5,86.6,152.9,1426,72.2,null,null,0.5]
[77,399.7,127,4.3899999999999997,81.599999999999994,"2009-02-11T11:05:38",72.2,399.7,12.7,439,8.0299999999999994,5.4999999999999997E-3,81.599999999999994,86.7,152.69999999999999,1109,72.2,null,null,0.5]
[77.5,400.7,128,4.5,81.400000000000006,"2009-02-11T11:06:10",73.599999999999994,400.7,12.8,450,7.89,5.7000000000000002E-3,81.400000000000006,86.5,157.1,1157,73.599999999999994,null,null,0.49]
[78,398.1,128,4.03,81.7,"2009-02-11T11:06:42",75.7,398.1,12.8,403,7.93,5.1000000000000004E-3,81.7,86.7,156.1,1032,75.7,null,null,0.48]
[78.5,387.6,128,4.26,82.1,"2009-02-11T11:07:14",76.3,387.6,12.8,426,7.96,5.4000000000000003E-3,82.1,87.2,155,1086,76.3,null,null,0.48]
[79,389.6,128,3.72,82,"2009-02-11T11:07:46",76.599999999999994,389.6,12.8,372,7.93,4.7000000000000002E-3,82,87.1,155.80000000000001,952,76.599999999999994,null,null,0.48]
[79.5,389.3,128,4.1399999999999997,82.1,"2009-02-11T11:08:18",77.099999999999994,389.3,12.8,414,7.94,5.1999999999999998E-3,82.1,87.1,155.80000000000001,1059,77.099999999999994,null,null,0.48]
[80,396.9,128,6.67,81.599999999999994,"2009-02-11T11:08:50",77.099999999999994,396.9,12.8,667,7.91,8.3999999999999995E-3,81.599999999999994,86.6,156.80000000000001,1713,77.099999999999994,null,null,0.47]
[80.5,396,129,5.0199999999999996,81.599999999999994,"2009-02-11T11:09:22",77.8,396,12.9,502,7.78,6.4000000000000003E-3,81.599999999999994,86.6,160.80000000000001,1309,77.8,null,null,0.47]
[81,395.3,129,4.29,81.599999999999994,"2009-02-11T11:09:54",77,395.3,12.9,429,7.79,5.4999999999999997E-3,81.599999999999994,86.7,160.69999999999999,1119,77,null,null,0.47]
[81.5,395.2,130,4.2,81.5,"2009-02-11T11:10:26",76.8,395.2,13,420,7.7,5.4999999999999997E-3,81.5,86.5,163.5,1107,76.8,null,null,0.47]
[82,403.8,129,3.52,81.400000000000006,"2009-02-11T11:10:58",77.2,403.8,12.9,352,7.81,4.4999999999999997E-3,81.400000000000006,86.4,160.1,915,77.2,null,null,0.47]
[82.5,401.1,130,2.56,81.400000000000006,"2009-02-11T11:11:30",77,401.1,13,256,7.73,3.3E-3,81.400000000000006,86.5,162.69999999999999,673,77,null,null,0.46]
[83,399.4,131,2.25,81.400000000000006,"2009-02-11T11:12:02",76.8,399.4,13.1,225,7.67,2.8999999999999998E-3,81.400000000000006,86.5,164.8,596,76.8,null,null,0.46]
[83.5,395.9,132,2.15,81.3,"2009-02-11T11:12:34",75.900000000000006,395.9,13.2,215,7.54,2.8999999999999998E-3,81.3,86.4,169.3,579,75.900000000000006,null,null,0.46]
[84,398,132,2.2599999999999998,81.3,"2009-02-11T11:13:06",78.099999999999994,398,13.2,226,7.52,3.0000000000000001E-3,81.3,86.3,169.9,610,78.099999999999994,null,null,0.46]
[84.5,396.1,133,1.63,81.400000000000006,"2009-02-11T11:13:38",80.3,396.1,13.3,163,7.45,2.2000000000000001E-3,81.400000000000006,86.4,172.6,444,80.3,null,null,0.46]
[85,403,134,2.2200000000000002,81,"2009-02-11T11:14:10",80,403,13.4,222,7.38,3.0000000000000001E-3,81,86,175.1,611,80,null,null,0.47]
[85.5,404.5,135,2.27,80.7,"2009-02-11T11:14:42",78.8,404.5,13.5,227,7.28,3.0999999999999999E-3,80.7,85.7,178.9,633,78.8,null,null,0.47]
[86,403.3,130,10.91,81,"2009-02-11T11:15:14",81.900000000000006,403.3,13,1091,7.74,1.41E-2,81,86,162.19999999999999,2860,81.900000000000006,null,null,0.47]
[86.5,394.4,126,14,81.7,"2009-02-11T11:15:46",82.2,394.4,12.6,1400,8.14,1.72E-2,81.7,86.8,149.30000000000001,3491,82.2,null,null,0.47]
[87,393.9,125,15.16,81.7,"2009-02-11T11:16:18",82.4,393.9,12.5,1516,8.18,1.8499999999999999E-2,81.7,86.8,148.19999999999999,3763,82.4,null,null,0.47]
[87.5,404.1,124,13.21,81.8,"2009-02-11T11:16:50",83.6,404.1,12.4,1321,8.35,1.5800000000000002E-2,81.8,86.8,143,3210,83.6,null,null,0.47]
[88,402.2,123,9.65,82.2,"2009-02-11T11:17:22",83.6,402.2,12.3,965,8.4499999999999993,1.14E-2,82.2,87.3,140.19999999999999,2318,83.6,null,null,0.47]
[88.5,395.8,123,6.54,82.5,"2009-02-11T11:17:54",83.1,395.8,12.3,654,8.3800000000000008,7.7999999999999996E-3,82.5,87.6,142.19999999999999,1584,83.1,null,null,0.47]
[89,398.4,124,4.2699999999999996,82.4,"2009-02-11T11:18:26",80.599999999999994,398.4,12.4,427,8.32,5.1000000000000004E-3,82.4,87.5,144,1042,80.599999999999994,null,null,0.47]
[89.5,394.7,124,4.21,82.4,"2009-02-11T11:18:58",77.8,394.7,12.4,421,8.35,5.0000000000000001E-3,82.4,87.5,143.19999999999999,1024,77.8,null,null,0.47]
[90,395,125,3.33,82.4,"2009-02-11T11:19:30",79.2,395,12.5,333,8.26,4.0000000000000001E-3,82.4,87.5,145.80000000000001,819,79.2,null,null,0.47]
[90.5,386.5,120,21.08,82.2,"2009-02-11T11:20:02",80.400000000000006,386.5,12,2108,8.68,2.4299999999999999E-2,82.2,87.3,133.69999999999999,4927,80.400000000000006,null,null,0.46]
[91,388.1,113,32.15,82.3,"2009-02-11T11:20:34",78.8,388.1,11.3,3215,9.42,3.4099999999999998E-2,82.3,87.4,115.5,6929,78.8,null,null,0.46]
[91.5,391.9,113,22.62,82.6,"2009-02-11T11:21:06",75.7,391.9,11.3,2262,9.41,2.4E-2,82.6,87.7,115.7,4880,75.7,null,null,0.45]
[92,389.7,115,19.98,82.5,"2009-02-11T11:21:38",73.7,389.7,11.5,1998,9.16,2.18E-2,82.5,87.6,121.6,4428,73.7,null,null,0.45]
[92.5,387.6,117,20.059999999999999,82.4,"2009-02-11T11:22:10",74.900000000000006,387.6,11.7,2006,9,2.23E-2,82.4,87.5,125.7,4527,74.900000000000006,null,null,0.45]
[93,396.7,118,16.670000000000002,82.3,"2009-02-11T11:22:42",79.5,396.7,11.8,1667,8.9,1.8700000000000001E-2,82.3,87.4,128,3802,79.5,null,null,0.45]
[93.5,399.3,120,13.85,82.2,"2009-02-11T11:23:14",82.3,399.3,12,1385,8.68,1.6E-2,82.2,87.3,133.9,3240,82.3,null,null,0.45]
[94,410.2,120,12.95,82,"2009-02-11T11:23:46",83.1,410.2,12,1295,8.68,1.49E-2,82,87,133.9,3029,83.1,null,null,0.45]
[94.5,392.3,122,12.6,82.4,"2009-02-11T11:24:18",84,392.3,12.2,1260,8.4700000000000006,1.49E-2,82.4,87.5,139.80000000000001,3022,84,null,null,0.44]
[95,392.6,124,13.12,82.2,"2009-02-11T11:24:50",84.1,392.6,12.4,1312,8.34,1.5699999999999999E-2,82.2,87.2,143.5,3195,84.1,null,null,0.44]
[95.5,395.3,126,10.66,82,"2009-02-11T11:25:22",84.1,395.3,12.6,1066,8.15,1.3100000000000001E-2,82,87.1,149.1,2655,84.1,null,null,0.44]
[96,{"$f":"FT","v":390},{"$f":"Oxy*10","v":127},{"$f":"CO/100","v":7.47},{"$f":"Effg","v":82.2},"2009-02-11T11:25:54",84.8,390,12.7,747,8.0299999999999994,9.2999999999999992E-3,82.2,87.3,152.69999999999999,1887,84.8,null,null,0.44]
[96.5,391.7,126,5.43,82.3,"2009-02-11T11:26:26",83.9,391.7,12.6,543,8.08,6.7000000000000002E-3,82.3,87.4,151.1,1364,83.9,null,null,0.44]
[97,402.2,127,2.66,82.1,"2009-02-11T11:26:58",84.9,402.2,12.7,266,8.0399999999999991,3.3E-3,82.1,87.2,152.4,671,84.9,null,null,0.44]
[97.5,393.3,127,2.35,82.4,"2009-02-11T11:27:30",84.2,393.3,12.7,235,8.02,2.8999999999999998E-3,82.4,87.5,153.1,595,84.2,null,null,0.44]
[98,396.5,126,3.54,82.4,"2009-02-11T11:28:02",85.5,396.5,12.6,354,8.1199999999999992,4.4000000000000003E-3,82.4,87.5,150.1,885,85.5,null,null,0.44]
[98.5,403.6,122,10.3,82.2,"2009-02-11T11:28:34",83.6,403.6,12.2,1030,8.52,1.21E-2,82.2,87.2,138.4,2455,83.6,null,null,0.45]
[99,408.5,123,5.16,82.2,"2009-02-11T11:29:06",84.4,408.5,12.3,516,8.44,6.1000000000000004E-3,82.2,87.3,140.5,1241,84.4,null,null,0.44]
[99.5,401.7,125,2.19,82.3,"2009-02-11T11:29:38",80.2,401.7,12.5,219,8.26,2.7000000000000001E-3,82.3,87.4,145.69999999999999,538,80.2,null,null,0.44]
[100,410.8,123,1.56,82.3,"2009-02-11T11:30:10",84.1,410.8,12.3,156,8.3800000000000008,1.9E-3,82.3,87.4,142.30000000000001,378,84.1,null,null,0.45]
[100.5,409.2,126,1.23,81.900000000000006,"2009-02-11T11:30:42",83.1,409.2,12.6,123,8.07,1.5E-3,81.900000000000006,87,151.4,309,83.1,null,null,0.44]
[101,408.2,130,0.74,81.599999999999994,"2009-02-11T11:31:14",85.4,408.2,13,74,7.74,1E-3,81.599999999999994,86.7,162.4,194,85.4,null,null,0.45]
[101.5,411.3,131,1.26,81.400000000000006,"2009-02-11T11:31:46",86.6,411.3,13.1,126,7.63,1.6999999999999999E-3,81.400000000000006,86.4,166.2,335,86.6,null,null,0.45]
[102,407.2,126,15.48,81.3,"2009-02-11T11:32:18",85.5,407.2,12.6,1548,8.1199999999999992,1.9099999999999999E-2,81.3,86.3,149.9,3869,85.5,null,null,0.46]
[102.5,396.7,128,8.77,81.7,"2009-02-11T11:32:50",85.2,396.7,12.8,877,7.9,1.11E-2,81.7,86.8,157,2254,85.2,null,null,0.44]
[103,402.6,135,5.8,80.8,"2009-02-11T11:33:22",85.1,402.6,13.5,580,7.28,8.0000000000000002E-3,80.8,85.8,178.8,1617,85.1,null,null,0.44]
[103.5,399.8,163,5.07,73.599999999999994,"2009-02-11T11:33:54",84.6,399.8,16.3,507,4.51,1.12E-2,73.599999999999994,78.2,350,2281,84.6,null,null,0.45]
[104,376.4,148,1.73,79.5,"2009-02-11T11:34:26",80.599999999999994,376.4,14.8,173,5.96,2.8999999999999998E-3,79.5,84.4,240.7,589,80.599999999999994,null,null,0.45]
[104.5,388.9,139,1.94,80.8,"2009-02-11T11:34:58",80.900000000000006,388.9,13.9,194,6.89,2.8E-3,80.8,85.8,194.4,571,80.900000000000006,null,null,0.45]
[105,394.9,137,3.39,80.599999999999994,"2009-02-11T11:35:30",78.599999999999994,394.9,13.7,339,7.05,4.7999999999999996E-3,80.599999999999994,85.6,188,976,78.599999999999994,null,null,0.45]
[105.5,405,135,4.3499999999999996,80.3,"2009-02-11T11:36:02",77.099999999999994,405,13.5,435,7.21,6.0000000000000001E-3,80.3,85.3,181.6,1225,77.099999999999994,null,null,0.46]
[106,389.3,139,5.56,80.5,"2009-02-11T11:36:34",80.599999999999994,389.3,13.9,556,6.9,8.0999999999999996E-3,80.5,85.5,194.1,1635,80.599999999999994,null,null,0.47]
[106.5,396,140,6.59,79.7,"2009-02-11T11:37:06",78,396,14,659,6.74,9.7999999999999997E-3,79.7,84.6,201.4,1986,78,null,null,0.45]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.5,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.400000000000006,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.400000000000006,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.599999999999994,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.8,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.2,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.099999999999994,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.7,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.099999999999994,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.8,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.2,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,61.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.1,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.900000000000006,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.8,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.599999999999994,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.599999999999994,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.400000000000006,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.900000000000006,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.400000000000006,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,66,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,null,null,0.4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]