{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Online"],"not_rendered":{"charts":1,"images":0,"macros":0,"external_links":0,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Online","index":0,"n_rows":246,"n_cols":20,"rows_kept":246,"cut":false,"hidden":false,"merged":[]}
["Minutes","°F FT","% O2x10","% COx100","% Effg","Date / time","°F AT","°F FT","% O2","ppm CO","% CO2","ratio","% Effg","% Effn","% ExAir","ppm uCO","°F AT","ppm amCO2","ppm amCO","l/min Pump"]
[null,{"$f":"AVERAGE(FT)","v":422.50934065934041},{"$f":"AVERAGE(Oxy)","v":12.240659340659342},{"$f":"AVERAGE(CO)","v":1794.7142857142858},{"$f":"AVERAGE(Effg)","v":79.566666666666691}]
[18.5,{"$f":"FT","v":198.4},{"$f":"Oxy*10","v":209},{"$f":"CO/100","v":2.16},{"$f":"Effg","v":0},"2009-02-22T20:10:17",63.3,198.4,20.9,216,null,null,null,null,null,null,63.3,null,null,0.55000000000000004]
[19,211.9,203,9.68,0,"2009-02-22T20:10:47",61,211.9,20.3,968,null,null,null,null,null,null,61,null,null,0.47]
[19.5,236,183,12.68,73.099999999999994,"2009-02-22T20:11:17",62.5,236,18.3,1268,2.62,4.8399999999999999E-2,73.099999999999994,77.599999999999994,675.6,9835,62.5,null,null,0.47]
[20,247.9,169,8.86,79.400000000000006,"2009-02-22T20:11:47",62,247.9,16.899999999999999,886,3.94,2.2499999999999999E-2,79.400000000000006,84.3,415.7,4569,62,null,null,0.44]
[20.5,264.60000000000002,158,9.7799999999999994,81.400000000000006,"2009-02-22T20:12:17",62.1,264.60000000000002,15.8,978,5.0599999999999996,1.9300000000000001E-2,81.400000000000006,86.5,301,3922,62.1,null,null,0.43]
[21,270.5,150,14.85,82.2,"2009-02-22T20:12:47",62.2,270.5,15,1485,5.81,2.5600000000000001E-2,82.2,87.3,249.4,5189,62.2,null,null,0.43]
[21.5,272.39999999999998,151,15.37,81.8,"2009-02-22T20:13:17",61.7,272.39999999999998,15.1,1537,5.69,2.7E-2,81.8,86.9,256.60000000000002,5481,61.7,null,null,0.43]
[22,278.39999999999998,154,15.44,81,"2009-02-22T20:13:47",62.2,278.39999999999998,15.4,1544,5.46,2.8299999999999999E-2,81,86,272.10000000000002,5745,62.2,null,null,0.44]
[22.5,280.60000000000002,152,13.11,81.5,"2009-02-22T20:14:17",61.8,280.60000000000002,15.2,1311,5.64,2.3300000000000001E-2,81.5,86.5,260.2,4722,61.8,null,null,0.44]
[23,279.60000000000002,157,4.03,81.3,"2009-02-22T20:14:47",61.3,279.60000000000002,15.7,403,5.12,7.9000000000000008E-3,81.3,86.3,296.3,1597,61.3,null,null,0.45]
[23.5,282.8,162,2.79,79.900000000000006,"2009-02-22T20:15:17",61.1,282.8,16.2,279,4.6100000000000003,6.1000000000000004E-3,79.900000000000006,84.8,340.5,1229,61.1,null,null,0.46]
[24,287.7,163,2.99,79.400000000000006,"2009-02-22T20:15:47",61.8,287.7,16.3,299,4.53,6.6E-3,79.400000000000006,84.3,348.5,1341,61.8,null,null,0.46]
[24.5,289,165,3.68,78.599999999999994,"2009-02-22T20:16:17",61.1,289,16.5,368,4.3499999999999996,8.5000000000000006E-3,78.599999999999994,83.5,366.9,1718,61.1,null,null,0.46]
[25,292.89999999999998,164,3.16,78.900000000000006,"2009-02-22T20:16:47",62.7,292.89999999999998,16.399999999999999,316,4.47,7.1000000000000004E-3,78.900000000000006,83.8,354.6,1437,62.7,null,null,0.46]
[25.5,298.60000000000002,162,3.27,79.099999999999994,"2009-02-22T20:17:17",62.3,298.60000000000002,16.2,327,4.66,7.0000000000000001E-3,79.099999999999994,84,335.2,1423,62.3,null,null,0.46]
[26,299.7,160,3.3,79.7,"2009-02-22T20:17:47",63.4,299.7,16,330,4.8600000000000003,6.7999999999999996E-3,79.7,84.6,317.60000000000002,1378,63.4,null,null,0.46]
[26.5,299.8,160,4.5,79.3,"2009-02-22T20:18:17",62.5,299.8,16,450,4.79,9.4000000000000004E-3,79.3,84.2,323.89999999999998,1908,62.5,null,null,0.46]
[27,299.2,161,6.93,79.099999999999994,"2009-02-22T20:18:47",63.2,299.2,16.100000000000001,693,4.7699999999999996,1.4500000000000001E-2,79.099999999999994,84,325.2,2947,63.2,null,null,0.46]
[27.5,299.39999999999998,162,7.19,78.599999999999994,"2009-02-22T20:19:17",62.8,299.39999999999998,16.2,719,4.6500000000000004,1.55E-2,78.599999999999994,83.5,336.9,3141,62.8,null,null,0.47]
[28,305.60000000000002,163,7.77,77.8,"2009-02-22T20:19:47",61.5,305.60000000000002,16.3,777,4.57,1.7000000000000001E-2,77.8,82.7,344.4,3453,61.5,null,null,0.47]
[28.5,300.8,165,9.9700000000000006,77.099999999999994,"2009-02-22T20:20:17",62.5,300.8,16.5,997,4.33,2.3E-2,77.099999999999994,81.900000000000006,368.7,4673,62.5,null,null,0.47]
[29,301.5,166,13.21,76.5,"2009-02-22T20:20:47",62.4,301.5,16.600000000000001,1321,4.2699999999999996,3.09E-2,76.5,81.2,375.3,6279,62.4,null,null,0.47]
[29.5,302.3,164,13.98,76.8,"2009-02-22T20:21:17",62.3,302.3,16.399999999999999,1398,4.41,3.1699999999999999E-2,76.8,81.599999999999994,360.7,6441,62.3,null,null,0.46]
[30,304.10000000000002,165,13,76.7,"2009-02-22T20:21:47",61.8,304.10000000000002,16.5,1300,4.37,2.9700000000000001E-2,76.7,81.400000000000006,364.2,6035,61.8,null,null,0.46]
[30.5,304.3,164,10.76,77.099999999999994,"2009-02-22T20:22:17",62.4,304.3,16.399999999999999,1076,4.41,2.4400000000000002E-2,77.099999999999994,81.900000000000006,360.6,4956,62.4,null,null,0.46]
[31,306,165,9.82,77,"2009-02-22T20:22:47",62.1,306,16.5,982,4.3899999999999997,2.24E-2,77,81.8,362.7,4544,62.1,null,null,0.46]
[31.5,307.39999999999998,162,9.42,77.900000000000006,"2009-02-22T20:23:17",62.4,307.39999999999998,16.2,942,4.6500000000000004,2.0299999999999999E-2,77.900000000000006,82.7,336.5,4112,62.4,null,null,0.45]
[32,{"$f":"FT","v":315.3},{"$f":"Oxy*10","v":157},{"$f":"CO/100","v":7.86},{"$f":"Effg","v":78.900000000000006},"2009-02-22T20:23:47",62.4,315.3,15.7,786,5.09,1.54E-2,78.900000000000006,83.8,298.8,3135,62.4,null,null,0.45]
[32.5,308.5,156,6.3,79.900000000000006,"2009-02-22T20:24:17",62.5,308.5,15.6,630,5.27,1.2E-2,79.900000000000006,84.8,285.39999999999998,2428,62.5,null,null,0.45]
[33,311.89999999999998,156,7.65,79.5,"2009-02-22T20:24:47",62.1,311.89999999999998,15.6,765,5.24,1.46E-2,79.5,84.4,287.2,2962,62.1,null,null,0.44]
[33.5,313.39999999999998,155,8.27,79.5,"2009-02-22T20:25:17",61.8,313.39999999999998,15.5,827,5.3,1.5599999999999999E-2,79.5,84.4,282.89999999999998,3167,61.8,null,null,0.45]
[34,311.3,156,7.69,79.400000000000006,"2009-02-22T20:25:47",61.8,311.3,15.6,769,5.2,1.4800000000000001E-2,79.400000000000006,84.3,290.10000000000002,2999,61.8,null,null,0.44]
[34.5,309.60000000000002,156,8.01,79.599999999999994,"2009-02-22T20:26:17",62.8,309.60000000000002,15.6,801,5.22,1.5299999999999999E-2,79.599999999999994,84.5,288.7,3114,62.8,null,null,0.45]
[35,315.60000000000002,155,7.77,79.5,"2009-02-22T20:26:47",62.6,315.60000000000002,15.5,777,5.32,1.46E-2,79.5,84.4,281.39999999999998,2963,62.6,null,null,0.45]
[35.5,320.3,147,9.14,80.900000000000006,"2009-02-22T20:27:17",62.2,320.3,14.7,914,6.1,1.4999999999999999E-2,80.900000000000006,85.9,233,3044,62.2,null,null,0.44]
[36,331,139,9.99,81.8,"2009-02-22T20:27:47",63.7,331,13.9,999,6.88,1.4500000000000001E-2,81.8,86.9,195.1,2948,63.7,null,null,0.43]
[36.5,332.9,137,12.4,81.7,"2009-02-22T20:28:17",61.8,332.9,13.7,1240,7.06,1.7600000000000001E-2,81.7,86.8,187.4,3564,61.8,null,null,0.43]
[37,339,137,15.97,81.3,"2009-02-22T20:28:47",62.9,339,13.7,1597,7.1,2.2499999999999999E-2,81.3,86.4,185.8,4565,62.9,null,null,0.43]
[37.5,331.8,134,18.25,81.900000000000006,"2009-02-22T20:29:17",63.1,331.8,13.4,1825,7.34,2.4899999999999999E-2,81.900000000000006,86.9,176.5,5046,63.1,null,null,0.43]
[38,343,133,23.45,81.3,"2009-02-22T20:29:47",63.5,343,13.3,2345,7.45,3.15E-2,81.3,86.3,172.3,6386,63.5,null,null,0.43]
[38.5,347.7,131,27.37,81.099999999999994,"2009-02-22T20:30:17",63.7,347.7,13.1,2737,7.65,3.5799999999999998E-2,81.099999999999994,86.2,165.2,7259,63.7,null,null,0.43]
[39,354,128,28.62,81.2,"2009-02-22T20:30:47",63.2,354,12.8,2862,7.95,3.5999999999999997E-2,81.2,86.3,155.19999999999999,7304,63.2,null,null,0.43]
[39.5,349.7,127,28.23,81.599999999999994,"2009-02-22T20:31:17",63.4,349.7,12.7,2823,8.0500000000000007,3.5099999999999999E-2,81.599999999999994,86.6,152.1,7116,63.4,null,null,0.42]
[40,359.7,123,29.35,81.599999999999994,"2009-02-22T20:31:47",63,359.7,12.3,2935,8.42,3.49E-2,81.599999999999994,86.7,141.19999999999999,7079,63,null,null,0.42]
[40.5,369.3,119,26.96,82,"2009-02-22T20:32:17",64,369.3,11.9,2696,8.83,3.0499999999999999E-2,82,87.1,130,6199,64,null,null,0.41]
[41,371.6,118,28.38,81.900000000000006,"2009-02-22T20:32:47",63,371.6,11.8,2838,8.89,3.1899999999999998E-2,81.900000000000006,87,128.4,6481,63,null,null,0.41]
[41.5,370.9,125,13.6,81.900000000000006,"2009-02-22T20:33:17",61.7,370.9,12.5,1360,8.2100000000000009,1.66E-2,81.900000000000006,86.9,147.30000000000001,3363,61.7,null,null,0.41]
[42,365.1,133,9.73,81.400000000000006,"2009-02-22T20:33:47",63.7,365.1,13.3,973,7.48,1.2999999999999999E-2,81.400000000000006,86.4,171.5,2641,63.7,null,null,0.4]
[42.5,364.4,133,8.76,81.400000000000006,"2009-02-22T20:34:17",63.1,364.4,13.3,876,7.42,1.18E-2,81.400000000000006,86.4,173.6,2397,63.1,null,null,0.4]
[43,370,131,8.7899999999999991,81.400000000000006,"2009-02-22T20:34:47",64.099999999999994,370,13.1,879,7.59,1.1599999999999999E-2,81.400000000000006,86.5,167.5,2351,64.099999999999994,null,null,0.41]
[43.5,372.1,126,8.5,82.2,"2009-02-22T20:35:17",64,372.1,12.6,850,8.16,1.04E-2,82.2,87.3,148.69999999999999,2114,64,null,null,0.41]
[44,375.2,121,13.48,82.4,"2009-02-22T20:35:47",64.400000000000006,375.2,12.1,1348,8.6300000000000008,1.5599999999999999E-2,82.4,87.5,135.1,3169,64.400000000000006,null,null,0.4]
[44.5,381.5,117,20.329999999999998,82.1,"2009-02-22T20:36:17",63.6,381.5,11.7,2033,8.9600000000000009,2.2700000000000001E-2,82.1,87.2,126.6,4606,63.6,null,null,0.41]
[45,376.3,116,27.9,82.1,"2009-02-22T20:36:47",63.9,376.3,11.6,2790,9.11,3.0599999999999999E-2,82.1,87.1,122.8,6215,63.9,null,null,0.4]
[45.5,383.1,113,35.03,81.8,"2009-02-22T20:37:17",63.4,383.1,11.3,3503,9.4,3.73E-2,81.8,86.8,116,7565,63.4,null,null,0.4]
[46,386.7,106,39.47,82.2,"2009-02-22T20:37:47",63.7,386.7,10.6,3947,10.050000000000001,3.9300000000000002E-2,82.2,87.3,102,7975,63.7,null,null,0.4]
[46.5,388.4,93,51.08,82.7,"2009-02-22T20:38:17",61.8,388.4,9.3000000000000007,5108,11.3,4.5199999999999997E-2,82.7,87.8,79.7,9180,61.8,null,null,0.42]
[47,401.3,88,60,82.5,"2009-02-22T20:38:47",61.2,401.3,8.8000000000000007,6000,11.82,5.0799999999999998E-2,82.5,87.6,71.8,10306,61.2,null,null,0.4]
[47.5,404,83,60,82.8,"2009-02-22T20:39:17",60.9,404,8.3000000000000007,6000,12.3,4.8800000000000003E-2,82.8,87.9,65,9903,60.9,null,null,0.4]
[48,408.6,82,80,82,"2009-02-22T20:39:47",61.5,408.6,8.1999999999999993,8000,12.37,6.4699999999999994E-2,82,87,64.2,13133,61.5,null,null,0.4]
[48.5,403.8,80,90,81.900000000000006,"2009-02-22T20:40:17",61.3,403.8,8,9000,12.61,7.1400000000000005E-2,81.900000000000006,87,61,14493,61.3,null,null,0.4]
[49,410.5,81,90,81.599999999999994,"2009-02-22T20:40:47",61.6,410.5,8.1,9000,12.48,7.2099999999999997E-2,81.599999999999994,86.7,62.6,14636,61.6,null,null,0.41]
[49.5,407.6,82,70,82.4,"2009-02-22T20:41:17",61.7,407.6,8.1999999999999993,7000,12.42,5.6399999999999999E-2,82.4,87.5,63.4,11440,61.7,null,null,0.41]
[50,408,84,60,82.6,"2009-02-22T20:41:47",61.8,408,8.4,6000,12.22,4.9099999999999998E-2,82.6,87.7,66.099999999999994,9967,61.8,null,null,0.41]
[50.5,411.3,87,60,82.3,"2009-02-22T20:42:17",61.4,411.3,8.6999999999999993,6000,11.89,5.0500000000000003E-2,82.3,87.4,70.7,10241,61.4,null,null,0.41]
[51,409.6,86,60,82.4,"2009-02-22T20:42:47",61.9,409.6,8.6,6000,11.96,5.0200000000000002E-2,82.4,87.5,69.7,10183,61.9,null,null,0.4]
[51.5,414.3,86,60,82.3,"2009-02-22T20:43:17",61.5,414.3,8.6,6000,11.98,5.0099999999999999E-2,82.3,87.4,69.400000000000006,10167,61.5,null,null,0.39]
[52,415.1,87,55,82.4,"2009-02-22T20:43:47",61.7,415.1,8.6999999999999993,5500,11.87,4.6300000000000001E-2,82.4,87.5,71.099999999999994,9408,61.7,null,null,0.4]
[52.5,421.3,88,50,82.4,"2009-02-22T20:44:17",61.9,421.3,8.8000000000000007,5000,11.82,4.2299999999999997E-2,82.4,87.5,71.7,8584,61.9,null,null,0.4]
[53,424.4,89,50,82.2,"2009-02-22T20:44:47",62.3,424.4,8.9,5000,11.73,4.2599999999999999E-2,82.2,87.3,73.099999999999994,8653,62.3,null,null,0.4]
[53.5,427.7,88,50,82.2,"2009-02-22T20:45:17",62.2,427.7,8.8000000000000007,5000,11.84,4.2200000000000001E-2,82.2,87.3,71.400000000000006,8571,62.2,null,null,0.4]
[54,428.2,85,55,82.2,"2009-02-22T20:45:47",62,428.2,8.5,5500,12.1,4.5499999999999999E-2,82.2,87.3,67.8,9227,62,null,null,0.41]
[54.5,428.3,81,55,82.5,"2009-02-22T20:46:17",62,428.3,8.1,5500,12.43,4.4200000000000003E-2,82.5,87.6,63.3,8982,62,null,null,0.4]
[55,429.2,84,55,82.3,"2009-02-22T20:46:47",62.4,429.2,8.4,5500,12.18,4.5199999999999997E-2,82.3,87.4,66.7,9168,62.4,null,null,0.4]
[55.5,433.3,89,55,81.8,"2009-02-22T20:47:17",62.4,433.3,8.9,5500,11.74,4.6800000000000001E-2,81.8,86.9,72.900000000000006,9510,62.4,null,null,0.4]
[56,430.1,89,50,82,"2009-02-22T20:47:47",62.4,430.1,8.9,5000,11.67,4.2799999999999998E-2,82,87.1,73.900000000000006,8695,62.4,null,null,0.41]
[56.5,431.2,89,50,82,"2009-02-22T20:48:17",61.6,431.2,8.9,5000,11.73,4.2599999999999999E-2,82,87.1,73.099999999999994,8654,61.6,null,null,0.42]
[57,433,88,50,82,"2009-02-22T20:48:47",62.6,433,8.8000000000000007,5000,11.75,4.2599999999999999E-2,82,87.1,72.8,8640,62.6,null,null,0.42]
[57.5,437.8,88,50,82,"2009-02-22T20:49:17",62.5,437.8,8.8000000000000007,5000,11.82,4.2299999999999997E-2,82,87,71.8,8588,62.5,null,null,0.42]
[58,434.6,85,50,82.3,"2009-02-22T20:49:47",62.4,434.6,8.5,5000,12.11,4.1300000000000003E-2,82.3,87.4,67.599999999999994,8380,62.4,null,null,0.43]
[58.5,438.1,83,19.77,83.6,"2009-02-22T20:50:17",62.5,438.1,8.3000000000000007,1977,12.28,1.61E-2,83.6,88.8,65.3,3268,62.5,null,null,0.39]
[59,448.3,82,28.52,83.1,"2009-02-22T20:50:47",62.7,448.3,8.1999999999999993,2852,12.38,2.3E-2,83.1,88.2,64,4678,62.7,null,null,0.39]
[59.5,443.9,84,32.49,82.9,"2009-02-22T20:51:17",62.9,443.9,8.4,3249,12.22,2.6599999999999999E-2,82.9,88,66.099999999999994,5398,62.9,null,null,0.39]
[60,451.5,81,30.27,83.1,"2009-02-22T20:51:47",65.2,451.5,8.1,3027,12.51,2.4199999999999999E-2,83.1,88.2,62.3,4912,65.2,null,null,0.39]
[60.5,455,84,25.05,83,"2009-02-22T20:52:17",66.5,455,8.4,2505,12.19,2.0500000000000001E-2,83,88.1,66.5,4171,66.5,null,null,0.4]
[61,453.3,84,21.5,83.2,"2009-02-22T20:52:47",67.400000000000006,453.3,8.4,2150,12.19,1.7600000000000001E-2,83.2,88.4,66.5,3580,67.400000000000006,null,null,0.39]
[61.5,448.6,85,23.46,83.2,"2009-02-22T20:53:17",66.8,448.6,8.5,2346,12.1,1.9400000000000001E-2,83.2,88.3,67.8,3937,66.8,null,null,0.39]
[62,455.5,86,24.45,82.9,"2009-02-22T20:53:47",67.7,455.5,8.6,2445,11.96,2.0400000000000001E-2,82.9,88,69.7,4149,67.7,null,null,0.39]
[62.5,456.6,84,23.95,82.9,"2009-02-22T20:54:17",65.7,456.6,8.4,2395,12.14,1.9699999999999999E-2,82.9,88.1,67.2,4004,65.7,null,null,0.39]
[63,458.1,82,20.82,83.2,"2009-02-22T20:54:47",66.400000000000006,458.1,8.1999999999999993,2082,12.35,1.6899999999999998E-2,83.2,88.4,64.400000000000006,3423,66.400000000000006,null,null,0.39]
[63.5,460.7,85,11.92,83.3,"2009-02-22T20:55:17",67.400000000000006,460.7,8.5,1192,12.06,9.9000000000000008E-3,83.3,88.5,68.3,2006,67.400000000000006,null,null,0.4]
[64,{"$f":"FT","v":458.9},{"$f":"Oxy*10","v":86},{"$f":"CO/100","v":10.41},{"$f":"Effg","v":83.4},"2009-02-22T20:55:47",68,458.9,8.6,1041,11.98,8.6999999999999994E-3,83.4,88.6,69.5,1764,68,null,null,0.39]
[64.5,467.5,87,11.8,83.1,"2009-02-22T20:56:17",68,467.5,8.6999999999999993,1180,11.94,9.9000000000000008E-3,83.1,88.2,70,2007,68,null,null,0.39]
[65,468.7,85,12.87,83.2,"2009-02-22T20:56:47",68.900000000000006,468.7,8.5,1287,12.13,1.06E-2,83.2,88.3,67.400000000000006,2154,68.900000000000006,null,null,0.4]
[65.5,464.5,85,13.44,83.2,"2009-02-22T20:57:17",68.099999999999994,464.5,8.5,1344,12.08,1.11E-2,83.2,88.4,68.099999999999994,2259,68.099999999999994,null,null,0.4]
[66,469.8,81,17.79,83.2,"2009-02-22T20:57:47",69.400000000000006,469.8,8.1,1779,12.44,1.43E-2,83.2,88.4,63.2,2903,69.400000000000006,null,null,0.39]
[66.5,471.9,78,21.69,83.2,"2009-02-22T20:58:17",68.5,471.9,7.8,2169,12.75,1.7000000000000001E-2,83.2,88.3,59.2,3452,68.5,null,null,0.39]
[67,476.2,80,21.42,83,"2009-02-22T20:58:47",69.3,476.2,8,2142,12.56,1.7100000000000001E-2,83,88.1,61.6,3461,69.3,null,null,0.39]
[67.5,475.9,83,20.73,82.8,"2009-02-22T20:59:17",68.400000000000006,475.9,8.3000000000000007,2073,12.26,1.6899999999999998E-2,82.8,87.9,65.5,3432,68.400000000000006,null,null,0.38]
[68,476.3,86,16.04,82.8,"2009-02-22T20:59:47",69.5,476.3,8.6,1604,12,1.34E-2,82.8,87.9,69.2,2714,69.5,null,null,0.38]
[68.5,476.2,87,12.52,82.8,"2009-02-22T21:00:17",65.8,476.2,8.6999999999999993,1252,11.93,1.0500000000000001E-2,82.8,87.9,70.099999999999994,2130,65.8,null,null,0.39]
[69,480.7,90,14.99,82.2,"2009-02-22T21:00:47",65.3,480.7,9,1499,11.57,1.2999999999999999E-2,82.2,87.3,75.400000000000006,2629,65.3,null,null,0.39]
[69.5,486,92,10.3,82.1,"2009-02-22T21:01:17",64.7,486,9.1999999999999993,1030,11.39,8.9999999999999993E-3,82.1,87.2,78.3,1836,64.7,null,null,0.36]
[70,483.1,94,7.16,82.2,"2009-02-22T21:01:47",66.7,483.1,9.4,716,11.23,6.4000000000000003E-3,82.2,87.3,80.8,1295,66.7,null,null,0.37]
[70.5,479.1,96,5.32,82.3,"2009-02-22T21:02:17",67.3,479.1,9.6,532,11.06,4.7999999999999996E-3,82.3,87.4,83.6,977,67.3,null,null,0.36]
[71,480.9,98,7.4,81.900000000000006,"2009-02-22T21:02:47",66.900000000000006,480.9,9.8000000000000007,740,10.85,6.7999999999999996E-3,81.900000000000006,87,87.2,1385,66.900000000000006,null,null,0.37]
[71.5,482.9,98,7.36,81.900000000000006,"2009-02-22T21:03:17",67.599999999999994,482.9,9.8000000000000007,736,10.8,6.7999999999999996E-3,81.900000000000006,86.9,88,1384,67.599999999999994,null,null,0.36]
[72,482.5,101,8.02,81.599999999999994,"2009-02-22T21:03:47",67.400000000000006,482.5,10.1,802,10.57,7.6E-3,81.599999999999994,86.7,92,1540,67.400000000000006,null,null,0.36]
[72.5,488.6,102,4.57,81.5,"2009-02-22T21:04:17",67.7,488.6,10.199999999999999,457,10.46,4.4000000000000003E-3,81.5,86.5,94.2,887,67.7,null,null,0.36]
[73,480.1,103,5.08,81.599999999999994,"2009-02-22T21:04:47",68.099999999999994,480.1,10.3,508,10.33,4.8999999999999998E-3,81.599999999999994,86.7,96.4,998,68.099999999999994,null,null,0.36]
[73.5,483.8,105,9.0500000000000007,81,"2009-02-22T21:05:17",67.599999999999994,483.8,10.5,905,10.119999999999999,8.8999999999999999E-3,81,86.1,100.6,1815,67.599999999999994,null,null,0.36]
[74,487.8,107,4.1100000000000003,81,"2009-02-22T21:05:47",68,487.8,10.7,411,9.99,4.1000000000000003E-3,81,86.1,103.2,835,68,null,null,0.36]
[74.5,482.5,110,2.3199999999999998,81,"2009-02-22T21:06:17",69.3,482.5,11,232,9.6999999999999993,2.3999999999999998E-3,81,86,109.2,485,69.3,null,null,0.37]
[75,480.3,112,1.5,80.8,"2009-02-22T21:06:47",69.7,480.3,11.2,150,9.4700000000000006,1.6000000000000001E-3,80.8,85.9,114.5,322,69.7,null,null,0.38]
[75.5,485.9,114,1.24,80.400000000000006,"2009-02-22T21:07:17",70,485.9,11.4,124,9.24,1.2999999999999999E-3,80.400000000000006,85.4,119.6,272,70,null,null,0.38]
[76,489.6,113,1.32,80.400000000000006,"2009-02-22T21:07:47",68.099999999999994,489.6,11.3,132,9.34,1.4E-3,80.400000000000006,85.3,117.2,287,68.099999999999994,null,null,0.38]
[76.5,485.5,115,1.34,80.2,"2009-02-22T21:08:17",67.900000000000006,485.5,11.5,134,9.15,1.5E-3,80.2,85.2,121.9,297,67.900000000000006,null,null,0.37]
[77,482.6,115,1.46,80.400000000000006,"2009-02-22T21:08:47",71.3,482.6,11.5,146,9.15,1.6000000000000001E-3,80.400000000000006,85.4,121.9,324,71.3,null,null,0.38]
[77.5,484.2,115,4.42,80.099999999999994,"2009-02-22T21:09:17",66.599999999999994,484.2,11.5,442,9.18,4.7999999999999996E-3,80.099999999999994,85,121.1,977,66.599999999999994,null,null,0.37]
[78,487.5,115,6.83,79.900000000000006,"2009-02-22T21:09:47",67.099999999999994,487.5,11.5,683,9.1999999999999993,7.4000000000000003E-3,79.900000000000006,84.8,120.7,1507,67.099999999999994,null,null,0.37]
[78.5,486.3,116,5.77,79.8,"2009-02-22T21:10:17",65.7,486.3,11.6,577,9.08,6.4000000000000003E-3,79.8,84.7,123.6,1290,65.7,null,null,0.37]
[79,487.4,115,4.38,80,"2009-02-22T21:10:47",66.2,487.4,11.5,438,9.23,4.7000000000000002E-3,80,85,120,963,66.2,null,null,0.37]
[79.5,490.2,114,4.7300000000000004,80,"2009-02-22T21:11:17",67,490.2,11.4,473,9.25,5.1000000000000004E-3,80,84.9,119.4,1038,67,null,null,0.38]
[80,485.2,114,5.95,80.099999999999994,"2009-02-22T21:11:47",67.7,485.2,11.4,595,9.26,6.4000000000000003E-3,80.099999999999994,85.1,119.2,1304,67.7,null,null,0.36]
[80.5,492.6,113,5.72,80,"2009-02-22T21:12:17",67.2,492.6,11.3,572,9.35,6.1000000000000004E-3,80,85,117,1242,67.2,null,null,0.35]
[81,492.6,114,4.07,80,"2009-02-22T21:12:47",69.099999999999994,492.6,11.4,407,9.25,4.4000000000000003E-3,80,85,119.5,893,69.099999999999994,null,null,0.35]
[81.5,485.9,115,3.9,80.2,"2009-02-22T21:13:17",69.8,485.9,11.5,390,9.17,4.3E-3,80.2,85.1,121.3,863,69.8,null,null,0.35]
[82,490.4,117,4.82,79.7,"2009-02-22T21:13:47",69.599999999999994,490.4,11.7,482,9.02,5.3E-3,79.7,84.7,125.2,1085,69.599999999999994,null,null,0.35]
[82.5,492.5,115,5.52,79.900000000000006,"2009-02-22T21:14:17",68.900000000000006,492.5,11.5,552,9.23,6.0000000000000001E-3,79.900000000000006,84.8,120,1214,68.900000000000006,null,null,0.35]
[83,496.6,113,3.78,80.099999999999994,"2009-02-22T21:14:47",68.900000000000006,496.6,11.3,378,9.36,4.0000000000000001E-3,80.099999999999994,85,116.8,819,68.900000000000006,null,null,0.35]
[83.5,495,112,3.38,80.2,"2009-02-22T21:15:17",68.900000000000006,495,11.2,338,9.43,3.5999999999999999E-3,80.2,85.2,115.3,728,68.900000000000006,null,null,0.35]
[84,497.2,113,2.5299999999999998,80,"2009-02-22T21:15:47",67.8,497.2,11.3,253,9.33,2.7000000000000001E-3,80,85,117.6,550,67.8,null,null,0.35]
[84.5,489.2,114,4.34,80.2,"2009-02-22T21:16:17",68.900000000000006,489.2,11.4,434,9.3000000000000007,4.7000000000000002E-3,80.2,85.1,118.3,947,68.900000000000006,null,null,0.35]
[85,486.9,112,9.1199999999999992,80.2,"2009-02-22T21:16:47",68.5,486.9,11.2,912,9.4700000000000006,9.5999999999999992E-3,80.2,85.2,114.4,1955,68.5,null,null,0.34]
[85.5,490.7,111,14.49,79.900000000000006,"2009-02-22T21:17:17",68.8,490.7,11.1,1449,9.59,1.5100000000000001E-2,79.900000000000006,84.9,111.8,3069,68.8,null,null,0.35]
[86,493.8,110,18.600000000000001,79.7,"2009-02-22T21:17:47",70.099999999999994,493.8,11,1860,9.64,1.9300000000000001E-2,79.7,84.7,110.5,3916,70.099999999999994,null,null,0.34]
[86.5,490.2,113,11.7,79.900000000000006,"2009-02-22T21:18:17",69.900000000000006,490.2,11.3,1170,9.42,1.24E-2,79.900000000000006,84.9,115.6,2522,69.900000000000006,null,null,0.34]
[87,484,113,8.34,80.2,"2009-02-22T21:18:47",69.5,484,11.3,834,9.3800000000000008,8.8999999999999999E-3,80.2,85.2,116.3,1804,69.5,null,null,0.34]
[87.5,492.8,113,9.7899999999999991,79.900000000000006,"2009-02-22T21:19:17",70,492.8,11.3,979,9.36,1.0500000000000001E-2,79.900000000000006,84.8,116.9,2124,70,null,null,0.34]
[88,491.7,114,10.62,79.8,"2009-02-22T21:19:47",71,491.7,11.4,1062,9.26,1.15E-2,79.8,84.7,119.2,2328,71,null,null,0.34]
[88.5,489.4,115,8.8000000000000007,79.900000000000006,"2009-02-22T21:20:17",71.3,489.4,11.5,880,9.2200000000000006,9.4999999999999998E-3,79.900000000000006,84.8,120.3,1938,71.3,null,null,0.34]
[89,493,119,5.19,79.400000000000006,"2009-02-22T21:20:47",69.599999999999994,493,11.9,519,8.82,5.8999999999999999E-3,79.400000000000006,84.3,130,1194,69.599999999999994,null,null,0.34]
[89.5,493.9,120,3.85,79.3,"2009-02-22T21:21:17",70.599999999999994,493.9,12,385,8.6999999999999993,4.4000000000000003E-3,79.3,84.2,133.30000000000001,898,70.599999999999994,null,null,0.34]
[90,498.5,123,5.15,78.599999999999994,"2009-02-22T21:21:47",70.599999999999994,498.5,12.3,515,8.4600000000000009,6.1000000000000004E-3,78.599999999999994,83.5,140.1,1236,70.599999999999994,null,null,0.34]
[90.5,501.1,124,3.38,78.3,"2009-02-22T21:22:17",69.900000000000006,501.1,12.4,338,8.27,4.1000000000000003E-3,78.3,83.2,145.5,830,69.900000000000006,null,null,0.34]
[91,494.3,127,2.83,78.2,"2009-02-22T21:22:47",70.8,494.3,12.7,283,8.01,3.5000000000000001E-3,78.2,83,153.30000000000001,717,70.8,null,null,0.34]
[91.5,497.2,127,2.96,78.099999999999994,"2009-02-22T21:23:17",70.599999999999994,497.2,12.7,296,8.01,3.7000000000000002E-3,78.099999999999994,82.9,153.4,750,70.599999999999994,null,null,0.34]
[92,497.9,128,3.49,77.900000000000006,"2009-02-22T21:23:47",71.400000000000006,497.9,12.8,349,7.95,4.4000000000000003E-3,77.900000000000006,82.7,155.5,892,71.400000000000006,null,null,0.34]
[92.5,500.6,128,3.62,77.8,"2009-02-22T21:24:17",70.900000000000006,500.6,12.8,362,7.93,4.5999999999999999E-3,77.8,82.6,156,927,70.900000000000006,null,null,0.34]
[93,494.9,128,3.31,77.900000000000006,"2009-02-22T21:24:47",70.7,494.9,12.8,331,7.9,4.1999999999999997E-3,77.900000000000006,82.8,156.80000000000001,850,70.7,null,null,0.33]
[93.5,497.7,129,4.26,77.599999999999994,"2009-02-22T21:25:17",70.7,497.7,12.9,426,7.8,5.4999999999999997E-3,77.599999999999994,82.4,160.1,1108,70.7,null,null,0.34]
[94,491.5,132,7.23,77.2,"2009-02-22T21:25:47",71.400000000000006,491.5,13.2,723,7.58,9.4999999999999998E-3,77.2,82,167.9,1937,71.400000000000006,null,null,0.34]
[94.5,497.7,133,7.22,76.7,"2009-02-22T21:26:17",70.5,497.7,13.3,722,7.46,9.7000000000000003E-3,76.7,81.400000000000006,172.3,1966,70.5,null,null,0.34]
[95,497.9,135,6.95,76.3,"2009-02-22T21:26:47",70.599999999999994,497.9,13.5,695,7.27,9.5999999999999992E-3,76.3,81,179.1,1940,70.599999999999994,null,null,0.33]
[95.5,497.5,136,6.56,76,"2009-02-22T21:27:17",69.900000000000006,497.5,13.6,656,7.16,9.1999999999999998E-3,76,80.8,183.5,1860,69.900000000000006,null,null,0.33]
[96,{"$f":"FT","v":499},{"$f":"Oxy*10","v":136},{"$f":"CO/100","v":6.83},{"$f":"Effg","v":75.900000000000006},"2009-02-22T21:27:47",69.8,499,13.6,683,7.14,9.5999999999999992E-3,75.900000000000006,80.599999999999994,184.5,1943,69.8,null,null,0.33]
[96.5,497.3,135,6.82,76.2,"2009-02-22T21:28:17",72,497.3,13.5,682,7.21,9.4999999999999998E-3,76.2,80.900000000000006,181.7,1921,72,null,null,0.33]
[97,501.9,140,6.73,75.099999999999994,"2009-02-22T21:28:47",71.599999999999994,501.9,14,673,6.81,9.9000000000000008E-3,75.099999999999994,79.7,198.2,2007,71.599999999999994,null,null,0.32]
[97.5,497.9,142,6.79,74.599999999999994,"2009-02-22T21:29:17",71.599999999999994,497.9,14.2,679,6.56,1.03E-2,74.599999999999994,79.2,209.3,2100,71.599999999999994,null,null,0.32]
[98,496.5,146,10.9,73,"2009-02-22T21:29:47",70.3,496.5,14.6,1090,6.14,1.77E-2,73,77.5,230.5,3602,70.3,null,null,0.33]
[98.5,487.8,149,10.9,72.599999999999994,"2009-02-22T21:30:17",71.099999999999994,487.8,14.9,1090,5.86,1.8599999999999998E-2,72.599999999999994,77,246.4,3776,71.099999999999994,null,null,0.32]
[99,488.4,150,10.88,72.2,"2009-02-22T21:30:47",70,488.4,15,1088,5.78,1.8800000000000001E-2,72.2,76.7,251.3,3822,70,null,null,0.32]
[99.5,489.4,151,12.18,71.7,"2009-02-22T21:31:17",70,489.4,15.1,1218,5.7,2.1399999999999999E-2,71.7,76.2,256.3,4339,70,null,null,0.32]
[100,492.6,152,13.93,71.099999999999994,"2009-02-22T21:31:47",69.099999999999994,492.6,15.2,1393,5.63,2.47E-2,71.099999999999994,75.5,260.7,5024,69.099999999999994,null,null,0.32]
[100.5,492,153,15.55,70.599999999999994,"2009-02-22T21:32:17",69.599999999999994,492,15.3,1555,5.52,2.8199999999999999E-2,70.599999999999994,75,268,5722,69.599999999999994,null,null,0.32]
[101,487,155,17.12,70.099999999999994,"2009-02-22T21:32:47",69.2,487,15.5,1712,5.36,3.1899999999999998E-2,70.099999999999994,74.400000000000006,278.60000000000002,6482,69.2,null,null,0.32]
[101.5,486.7,153,20.13,70.2,"2009-02-22T21:33:17",69.099999999999994,486.7,15.3,2013,5.46,3.6799999999999999E-2,70.2,74.5,271.5,7478,69.099999999999994,null,null,0.31]
[102,484.7,154,20,70,"2009-02-22T21:33:47",69.5,484.7,15.4,2000,5.38,3.7199999999999997E-2,70,74.3,277.3,7547,69.5,null,null,0.32]
[102.5,475.9,158,23.22,68.5,"2009-02-22T21:34:17",68.900000000000006,475.9,15.8,2322,5,4.6399999999999997E-2,68.5,72.7,305.7,9420,68.900000000000006,null,null,0.32]
[103,475.1,159,28.79,67.8,"2009-02-22T21:34:47",68.7,475.1,15.9,2879,4.97,5.79E-2,67.8,72,308.5,11761,68.7,null,null,0.32]
[103.5,487.4,158,32.49,66.900000000000006,"2009-02-22T21:35:17",69.400000000000006,487.4,15.8,3249,5,6.5000000000000002E-2,66.900000000000006,71.099999999999994,306.10000000000002,13193,69.400000000000006,null,null,0.31]
[104,458.1,176,14.41,59.1,"2009-02-22T21:35:47",70,458.1,17.600000000000001,1441,3.31,4.3499999999999997E-2,59.1,62.8,512.9,8831,70,null,null,0.32]
[104.5,450.9,146,8.06,75.5,"2009-02-22T21:36:17",68.099999999999994,450.9,14.6,806,6.22,1.2999999999999999E-2,75.5,80.099999999999994,226.6,2632,68.099999999999994,null,null,0.32]
[105,457.5,138,8.02,77.099999999999994,"2009-02-22T21:36:47",69.099999999999994,457.5,13.8,802,6.98,1.15E-2,77.099999999999994,81.900000000000006,190.7,2331,69.099999999999994,null,null,0.3]
[105.5,470,134,11.49,77.2,"2009-02-22T21:37:17",69.7,470,13.4,1149,7.38,1.5599999999999999E-2,77.2,82,175.2,3162,69.7,null,null,0.3]
[106,473.5,129,14.43,77.7,"2009-02-22T21:37:47",68.900000000000006,473.5,12.9,1443,7.79,1.8499999999999999E-2,77.7,82.5,160.69999999999999,3762,68.900000000000006,null,null,0.3]
[106.5,472,133,12.21,77.2,"2009-02-22T21:38:17",69.3,472,13.3,1221,7.42,1.6500000000000001E-2,77.2,82,173.6,3341,69.3,null,null,0.3]
[107,480.2,133,12.13,77,"2009-02-22T21:38:47",70.400000000000006,480.2,13.3,1213,7.44,1.6299999999999999E-2,77,81.7,173,3311,70.400000000000006,null,null,0.3]
[107.5,481.2,136,15.29,76.099999999999994,"2009-02-22T21:39:17",71.099999999999994,481.2,13.6,1529,7.15,2.1399999999999999E-2,76.099999999999994,80.8,183.8,4339,71.099999999999994,null,null,0.3]
[108,475.7,141,13.08,75.400000000000006,"2009-02-22T21:39:47",71.400000000000006,475.7,14.1,1308,6.68,1.9599999999999999E-2,75.400000000000006,80,204.1,3977,71.400000000000006,null,null,0.3]
[108.5,484.2,142,13.2,74.599999999999994,"2009-02-22T21:40:17",69.8,484.2,14.2,1320,6.57,2.01E-2,74.599999999999994,79.3,208.8,4076,69.8,null,null,0.31]
[109,486.5,145,14.72,73.5,"2009-02-22T21:40:47",68.599999999999994,486.5,14.5,1472,6.27,2.35E-2,73.5,78,223.8,4767,68.599999999999994,null,null,0.3]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,59,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,61,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.3,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60.8,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.5,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.400000000000006,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.400000000000006,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.599999999999994,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.8,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.2,null,null,0.37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.099999999999994,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.7,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.099999999999994,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.8,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.2,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,61.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.1,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.900000000000006,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.8,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62.9,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63.7,null,null,0.38]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.599999999999994,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64.599999999999994,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.400000000000006,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.900000000000006,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65.400000000000006,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,66,null,null,0.39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,null,null,0.4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]